## Schedules of Quantities
ELIDZ - FIRE EXTINGUISHERS, HOSE REELS AND HYDRANTS - 2021 TENDER
SCHEDULE 1 : PRELIMINARY & GENERAL ITEMS |  |  |  | Tender Price
Item | Description | Unit | Qty | Rates |  | Nett Amount
|  |  |  | Supply | Install
1 | PRELIMINARY & GENERAL
1.1 | Annual Contractual Items
1.1.1 | Provision of Sureties | Year | 3
1.1.2 | Provision of Insurances e.g. Contractor's All Risks, Public Liability, Plant and Equipment, Common Law Liability, etc. | Year | 3
1.1.3 | Allowance for Compliance with Construction Regulations, as detailed in Occupational Health & Safety Act, Act 85 of 1993 | Year | 3
1.1.4 | Provision of Compliance Certificates | Year | 3
1.1.5 | Other items not detailed above : specify _____________________________________________________________________________________________________________________________________________ | Year | 3
1.2 | Monthly Contractual Items
1.2.1 | Monthly overheads & administration charges | month | 36
1.2.2 | Other items not detailed above : specify _____________________________________________________________________________________________________________________________________________ | Year | 3
TOTAL FOR SCHEDULE 1 CARRIED FORWARD TO SUMMARY
ELIDZ - FIRE PREVENTION - 2021 TENDER
SCHEDULE 2 : ROUTINE MAINTENANCE |  |  |  | Tender Price
Item | Description | Unit | Qty | Rates |  | Nett Amount
|  |  |  | Supply | Install
2 | ROUTINE MAINTENANCE
Carry out inspections, repairs and servicing as detailed in the Scope of Works
2.1 | Scheduled Work - Installation Inspection
2.1.1 | Initial visual inspection at commencement of approximately 318 Fire Exinguishers, 71 Fire Hose Reels, 2 Portable Foam Equipment (Mobile Trolly Foam Extinguishers), 15 weatherproof enclosures, 39 Fire Hydrants and submit a verifiable asset register and condition report. | sum
2.2 | Scheduled Work - Quarterly Inspection
Quarterly visual inspection of approximately 318 Fire Exinguishers, 71 Fire Hose Reels, 2 Portable Foam Equipment (Mobile Trolly Foam Extinguishers), 15 weatherproof enclosures, 39 Fire Hydrants and submit a condition report reflecting all assets.
2.2.1 | Inspecting 2kg dry powder portable extinguishers | no. | 66
2.2.2 | Inspecting of 4,5kg CO2 portable extinguishers | no. | 1254
2.2.3 | Inspecting of 5kg CO2 portable extinguishers | no. | 7359
2.2.4 | Inspecting 9kg DCP portable extinguishers | no. | 1782
2.2.5 | Inspecting 9L Water expelled foam portable extinguishers | no. | 66
2.2.6 | Inspection of Galvanised fire hose reels with 30m hose and galvanised wall mounting brackets C/W holder bracket on chain with wheel for hose, shut off ball valve and aluminum nozzle | no. | 2556
2.2.7 | Monthly inspection of Internal and External Fire Hydrants, valves, pipework, gauges, etc. | no. | 1404
2.2.8 | Inspection of Weather proof fibreglass or poly carbonate fire extinguisher enclosures including cover for mounting of fire hose reels C/W padlocks and key holders | no. | 495
2.3 | Scheduled Work - Annual Servicing
Annual servicing of approximately 318 Fire Exinguishers, 71 Fire Hose Reels, 2 Portable Foam Equipment (Mobile Trolly Foam Extinguishers), 15 weatherproof enclosures, 39 Fire Hydrants and submit a condition report reflecting all assets.
2.3.1 | Annual Servicing of 2kg dry powder portable extinguishers | no. | 6
2.3.2 | Annual Servicing of 4,5kg CO2 portable extinguishers | no. | 114
2.3.3 | Servicing of 5kg CO2 portable extinguishers | no. | 669
2.3.4 | Annual Servicing of 9kg DCP portable extinguishers | no. | 162
2.3.5 | Annual Servicing of 9L Water expelled foam portable extinguishers | no. | 6
2.3.6 | Annual Servicing of Galvanised fire hose reels with 30m hose and galvanised wall mounting brackets C/W holder bracket on chain with wheel for hose, shut off ball valve and aluminum nozzle | no. | 213
2.3.7 | Provide flow test certificates of 30 litres/minute for each hose reel
2.3.8 | Annual Servicing of Internal and External Fire Hydrants, valves, pipework, gauges, etc, using appropriate tooling and testing equipment | no. | 117
2.3.9 | Provide flow test certificates of 1200 litres/minute for each hydrant | no. | 117
2.3.10 | Annual Inspection Service of Weather proof fibreglass or poly carbonate fire extinguisher enclosures including cover for mounting of fire hose reels C/W padlocks and key holders | no. | 45
TOTAL FOR SCHEDULE 2 CARRIED FORWARD TO SUMMARY
ELIDZ - FIRE PREVENTION - 2021 TENDER
SCHEDULE 3: CONTINGENCY ITEMS |  |  |  | Tender Price
Item | Description | Unit | Qty | Rates |  | Nett Amount
|  |  |  | Supply | Install
4 | CONTINGENCY ITEMS
4.1 | Related repair / servicing / installation / additional work required, as authorised by the client representative, not specifically detailed in Schedules 2 or 3 above | sum | 1 | 100000 | 0 | 100000
4.2 | Profit and attendance | sum | 1
TOTAL FOR SCHEDULE 4 CARRIED FORWARD TO SUMMARY
COSTING SUMMARY
Year 1
1 | PRELIMINARY & GENERAL
2 | ROUTINE MAINTENANCE
3 | CONTINGENCY ITEMS
Sub-total for Year 1, 2, 3
Allow 10% Escalation
Sub-total for Year 1,2,3
Add VAT @ 15%
Gross Tender Sum