## Blank_PS_BOQ
Item | Description | Unit | Qty | Supply Rate | Amount
SECTION A1 : ANNUAL CHARGES
A1.1 | Annual Preliminary & General
A1.1.1 | Provision of surety | Year | 1 | R | R
A1.1.2 | Provision of insurances | Year | 1 | R | R
A1.1.3 | Staff protective personal equipment | Year | 1 | R | R
A1.1.4 | Staff induction | Year | 1 | R | R
A1.1.5 | Initial OHS compliance | Year | 1 | R | R
A1.1.6 | Initial CEMP compliance | Year | 1 | R | R
A1.1.7 | Provision of Electronic Maintenance Manual | Year | 1 | R | R
A1.1.8 | Provision of Updated drawings in AutoCAD format | Year | 1 | R | R
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total | R
SECTION A2 : MONTHLY CHARGES
A2.1 | Monthly Preliminary & General
A2.1.1 | Monthly overheads & administration charges - Provide on site staff (1x Senior Technician/Foreman, 1x Semi-skilled/Jnr Techncian, 2 x General Hands) permanently on site during normal working hours to undertake the various maintenance and plant operation tasks as directed or required. | Months | 12 | R | R
A2.1.2 | Other contractual items not detailed above | Months | 12 | R | R
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total | 0
SECTION B1 : ROUTINE MAINTENANCE
B1 | Routine maintenance (inclusive of all labour, equipment, transport and related costs)
B1.1 | Complete monthly inspection & submit condition report of Z1A Indoor Waste Water Pump Station Assets | No. | 12 | R | R
B1.2 | Maintain/Support 2 x Gorman Rupp T6 Pumps, 2 x 37 KW Motors, 4 x N/R Valves, 2 x Isolation valves, Suction & Delivery Pipe work, 2 x Vacuum & 2 x Pressure Gauges, Protection, Support Brackets, Covers and Name Plates - Application of Tectyl Marine Grade Corrosion retardant, greasing and lubricating will be included in this activity | No. | 12 | R | R
B1.3 | Maintain/Support Huber Rotamat R02/1000/3 Screen including electrical control panel, water supply lines, jets, bearings and differential controls | No. | 12 | R | R
B1.4 | Maintain/Support Main Electrical Distribution Control Panel for the plant room including display indication, filtered ventilation, 2 x Siemens G120 variable speed drives, protection equipment, single line diagrams, terminal connections and general cleaning | No. | 12 | R | R
B1.5 | Maintain/Support/Calibrate Endress + Hauser Magflo, level, differential instrumentation including display modules, float levels, presuure transducer, control outputs, verification of I/O measurments required for Citect SCADA recordings & control | No. | 12 | R | R
B1.6 | Maintain/Support/Calibrate Endress + Hauser CE4 Measuring Station, including electronics, water sampler, analysis & protection instrumentation, pump, water supply, control outputs, verification of I/O measurments required for Citect SCADA recordings & control | No. | 12 | R | R
B1.7 | Maintain/Support Domestic Electrical installation including internal/external lighting, ventilation supplies, socket outlets, motor supplies, screen supply and CE4 measuring Station supply | No. | 12 | R | R
B1.8 | Cleaning of inlet channels and wet well sump | No. | 12 | R | R
|  |  |  | R | R
B1.25 | Complete monthly inspection & submit condition report of Complete Mariculture Sea Water Pump Station Assets - Including Reservoir Site, which details reconcilliation of water delivery and consumption data | No. | 12 | R | R
B1.26 | Maintain/Support 2 x ABS BE 425 - 2048 Pump Sets, 2 x 1LG4317 - 4AA60 - 2K20 + D60 200 KW Siemens Motors Size 315 L Therm CL 155 (F) IE1, 2 x Flygt BS 2720.390MT (241)Submersible Pumps, 1 x Submersible Pump, 4 x N/R Valves, 19 x Isolation Gate valves, 2 x Bermad Valves, Air valves All Pipe work inside the pump Station, All M&E Gauges, Fall Protection, Stairways, landings, Support Brackets, Covers and Name Plates - Application of Corrosion retardant, greasing and lubricating will be included in this activity | No. | 12 | R | R
B1.27 | Maintain/Support 2 x Hydrotech Drumfilters including electrical control panel, water supply lines, jets, bearings, filter panels and controls | No. | 12 | R | R
B1.28 | Maintain/Support/Calibrate All Control Instrumentation including display modules, float/ultrasonic levels, pressure transducer, control outputs, verification of I/O measurments required for Citect SCADA recordings & monitoring at the Reservoir Site | No. | 12 | R | R
B1.29 | Maintain/Support/Calibrate All Control Instrumentation including display modules, float/ultrasonic levels, pressure transducer, control outputs, verification of I/O measurments required for Citect SCADA recordings & monitoring at the Sea Water Pump Station | No. | 12 | R | R
B1.30 | Provide Annual certification for two (2) motorized winches and chains | No. | 1 | R | R
B1.31 | Maintain/Support two (2) motorized winches, including control wiring, lifting hooks, gantry and track | No. | 12 | R | R
B1.32 | Clear and remove Silt build-up around sea inlets cages in the gulley (anticipate 2 M3) twice a year, remove cages, place temporary screens, clean cages and re-install cages - remove any debris in the inlet pipework before installing cages back into position | No. | 1 | R | R
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total | R
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION C1 : GENERAL MAINTENANCE
C1 | General maintenance -inclusive of 24 hour response with ELIDZ control and security office(Supply rates - Don’t add the total for this section to the final total amount)
C1.1 | Siemens G120 variable speed drive | Qty | 1 | R | R
C1.2 | Siemens PLC | Qty | 1 | R | R
C1.3 | Mains Supply indication | Qty | 1 | R | R
C1.4 | FDU 80 instrument | Qty | 1 | R | R
C1.5 | FDU 80 display | Qty | 1 | R | R
C1.6 | Magflo meter | Qty | 1 | R | R
C1.7 | Paperless recorder | Qty | 1 | R | R
C1.8 | 24 Volt power supply | Qty | 1 | R | R
C1.9 | 24 Volt relays | Qty | 1 | R | R
C1.10 | 3 Phase 200A Isolator + interlock | Qty | 1 | R | R
C1.11 | 3 Phase 100 A MCB | Qty | 1 | R | R
C1.12 | 3 Phase 80 A MCB | Qty | 1 | R | R
C1.13 | 3 Phase 30 A MCB | Qty | 1 | R | R
C1.14 | 3 Phase 10 A MCB | Qty | 1 | R | R
C1.15 | 3 Phase Surge Protection | Qty | 1 | R | R
C1.16 | 3 Phase ELU 50 A | Qty | 1 | R | R
C1.17 | Single Phase ELU 60 A | Qty | 1 | R | R
C1.18 | Single Phase 30 A MCB | Qty | 1 | R | R
C1.19 | Single Phase 20 A MCB | Qty | 1 | R | R
C1.20 | Single Phase 10 A MCB | Qty | 1 | R | R
C1.21 | 60 A Welding Outlet | Qty | 1 | R | R
C1.22 | 16 A Single Switched Socket Outlet | Qty | 1 | R | R
C1.23 | 16 A Double Switched Socket Outlet | Qty | 1 | R | R
C1.24 | Type A - Nordland / JB258 / C21 / ECG / Warm Start / SS clips | Qty | 1 | R | R
C1.25 | 58 Watt Fluorescent Lamp 1.5m | Qty | 1 | R | R
C1.26 | 37 KW Siemens Motor | Qty | 1 | R | R
C1.27 | Complete Gorman Rupp T6 Pump Set with Balzona Lined Volute and Stainless Steel Impellor | Qty | 1 | R | R
C1.28 | Stainless Steel Impellor | Qty | 1 | R | R
C1.29 | Impellor Wear Plate | Qty | 1 | R | R
C1.30 | Impellor Seal | Qty | 1 | R | R
C1.31 | Inlet Non Return Valve | Qty | 1 | R | R
C1.32 | Exit Non Return Valve | Qty | 1 | R | R
C1.33 | Isolation Valve | Qty | 1 | R | R
C1.34 | Air Release valve | Qty | 1 | R | R
C1.35 | Inlet Pipe line | Qty | 1 | R | R
C1.36 | Vacuum Gauge | Qty | 1 | R | R
C1.37 | Pressure Gauge | Qty | 1 | R | R
C1.38 | V Belt | Qty | 1 | R | R
C1.39 | Six Point Inlet Flow Monitoring and Report for a week period with the aid of data logging equipment - data to be provided in electronic format for record / reference purposes and should include a reconcilliation report that details findings and recommendations explaining pumpstation outputs | Qty | 1 | R | R
SECTION A4 : PROVISIONAL CHARGES
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION D1 : PROVISIONAL SUMS
D1.1 | Call out (inclusive of all labour, equipment, transport and related costs)
D1.1.1 | Emergency response (Immediate) | No. | 480 | R | R
D1.1.2 | Urgent response (24 hours) | No. | 480 | R | R
D1.1.3 | Routine response (extra over during normal working hours) | No. | 480 | R | R
D1.2 | Labour additional to scheduled works
D1.2.1 | Mechanical Technician | hr | 600 | R | R
D1.2.2 | Semi Skilled Labour | hr | 600 | R | R
D1.2.3 | Labour | hr | 600 | R | R
D1.3 | Travelling additional to scheduled works
D1.3.1 | LDV | hr | 600 | R | R
D1.3.2 | Truck - 8 Ton | hr | 600 | R | R
D1.3.3 | Hydraulic Platform | hr | 5 | R | R
D1.3.4 | Crane truck | hr | 5 | R | R
D1.3.5 | Compressor | hr | 5 | R | R
D1.3.6 | Whacker Rammer Compactor | hr | 5 | R | R
D1.4 | All Provisional Allowances shall be expended solely at the discretion and on the instruction of the Employer's Agent
D1.4.1 | Contingency allowance for non-schedule Work | Sum | 1 | 200000 | 200000
D1.4.2 | Profit and Attendance | % |  | % | R
D1.4.3 | Provisional Sum for Employer's Agent(s) specialist input whenever/where required. | Sum | 4 | 60000 | 240000
D1.4.4 | Profit and Attendance | % |  | % | R
D1.4.5 | Provisional Sum for Waste Water Equipment | Sum | 1 | 500000 | 500000
D1.4.6 | Profit and Attendance | % |  | % | R
D1.4.5 | Provisional Sum for Mariculture Installation | Sum | 1 | 500000 | 500000
D1.4.6 | Profit and Attendance | % |  | % | R
D1.4.5 | Provisional Sum for Specialized Diving and Gulley Cleaning | Sum | 1 | 50000 | 50000
D1.4.6 | Profit and Attendance | % |  | % | R
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total | R
SUMMARY
| SECTION A1 : ANNUAL CHARGES |  |  |  | R
| SECTION A2 : MONTHLY CHARGES |  |  |  | R
| SECTION B1 : ROUTINE CHARGES |  |  |  | R
| SECTION D1 : PROVISIONAL SUMS |  |  |  | R
| Nett Tender Sum for Year 1 |  |  |  | R
| Nett Tender Sum for Year 2 (Escalated) |  |  | % | R
| Subtotal |  |  |  | R
| Add VAT @ 15% |  |  |  | R
| Gross Tender Sum carried to Form of Offer |  |  |  | R