## P & G
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
SCHEDULE NO 1: PRELIMINARY & GENERAL
ITEM
NO | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
TITY
1 | CONTRACTUAL CONDITIONS
1.1 | Compliance with General Conditions of Contract : Insurances, Sureties, etc as outlined in the Principal Contractor's Preliminaries.
1.2 | Establish on Site and provision of buildings and storage facilities including de-establishment of site, cleaning and tidying up after completion of contract
| Fixed | Item | 1
| Value Related | Item | 1
| Time Related | Item | 1
1.3 | Tools and equipment, Communication, transport.
| Fixed | Item | 1
| Value Related | Item | 1
| Time Related | Item | 1
1.4 | Contract Management, Company overheads and supervision of the Works including attendance of site meetings (2 per month)
| Fixed | Item | 1
| Value Related | Item | 1
| Time Related | Item | 1
| Attendance at site meetings | Sum | 1
1.5 | Provision of all drawings and manuals as specified including As-Installed drawings | Item | 1
1.6 | Liaison with Local Supply Authority, compliance with OSH Act, Local By-laws and any other statutory regulations | Item | 1
1.7 | DAYWORK SCHEDULE
Personnel
| Coded welder | hr
| Registered electrician | hr
| Registered HVAC technician | hr
| Apprentice | hr
| Labourer | hr
Carried forward
SCHEDULE NO 1: PRELIMINARY & GENERAL
ITEM | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
NO |  |  | TITY
Brought forward
1.9 | GUARANTEE
| 12 month guarantee of plant and | Sum | 1
equipment as specified
Allowance for servicing the plant
during the guarantee period
| Monthly service calls to check plant | No | 8
operation, clean filters, etc
| 3 monthly minor service as specified | No | 3
| Annual major service at the end of | No | 1
the guarantee period
1.10 | Additional Tests
Allow for aditional tests as direct by
| the Consulting Engineer | Item
1.11 | Additional items
Any additional items the contractor
wishes to allow for:
(Specify)
TOTAL SCHEDULE NO 1 - CARRIED TO SUMMARY

## Feltex AE1
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
FELTEX FACTORY AE1
Automatic Sprinkler System
| 7,2 | Sprinkler Valve Location Plate
|  | Valve location plate must be affixed on an external wall, as near to the main stop valve as possible. | No. | 1
| 7,3 | Fire Brigade Booster Pressure Limitation Plate
|  | Valve location plate must be affixed on an external wall, as near to the main stop valve as possible. | No. | 1
| 7,4 | Block Plan
|  | Provide new block plan, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be keyed alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 6
|  | Large - 36 heads 15 mm Diam | No. | 6
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK3542 | No. | 1
Sprinklers
Spare Sprinklers:
|  | ESFR VK3542 Conventional Spray 141 Deg C | No. | 54
Carried forward to Next Page
Carried forward from Previous Page
| 7,7; 8; 10; 14 & 20 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New bypass Valve 2 - 100mm Diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble & modify existing valves (100 diam . | No. | 1
| 7.12 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | PC SUM |  |  |  | 21000
| 7.16 | Gauge Cock Replacement
|  | Replace pressure gauge isolating gauge cock with bleed outlet | No. | 1
| 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1 & 2 | No. | 40
| 7,20 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 4
|  | - 25 diam elbows | No. | 7
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
|  | - 50 diam elbows | No. | 7
Carried forward to Next Page
Carried forward from Previous Page
| AE1 Issue 2 | Vertical supports for workshop area:
|  | - 80 mm pipe support | No. | 2
| AE1 Issue 3 | New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 24
|  | - 32 mm diam pipe | m | 24
|  | - 40 mm diam pipe | m | 12
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 6
|  | - 100 mm diam pipe | m | 24
|  | - 25 mm sprinkler equal Tee | No. | 4
|  | - 32 mm sprinkler reducing Tee | No. | 4
|  | - 40 mm sprinkler reducing Tee | No. | 4
|  | - 50 mm sprinkler reducing Tee | No. | 4
|  | - 32 - 25 mm diam reducers | No. | 4
|  | - 40 - 32 mm diam reducers | No. | 4
|  | - 50 - 40 mm diam reducers | No. | 4
|  | - 65 - 50 mm diam reducers | No. | 4
|  | - 80 - 65 mm diam reducers | No. | 4
|  | - 100 - 80 mm diam reducers | No. | 4
|  | - 80 mm diam equal tee | No. | 4
|  | - 100 mm diam equal tee | No. | 4
|  | ESFR VK3542 Conventional Spray 141 Deg C | No. | 5
| AE1 Issue 4 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 28
| AE1 Issue 5 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | PC SUM |  |  |  | 21000
| AE1 Issue 6 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
| AE1 Issue 7 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 97
|  | - Unistrut 41 x 41 mm | m | 242.5
|  | - Unistrut beam clamp | No. | 194
| AE1 Issue 15 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | PC SUM |  |  |  | 21000
| AE1 Issue 17 | Terminal Range Support
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 20
|  | - Unistrut 41 x 41 mm | m | 60
|  | - Unistrut beam clamp | No. | 40
| AE1 Issue 24 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | PC SUM |  |  |  | 21000
| AE1 Issue 25 | Pipe Supports
Receiving canopy. No support on the distribution mains
|  | - 100 mm pipe hangar; G clamp and hanging rod | No. | 22
|  | - Unistrut 41 x 41 mm | m | 66
|  | - Unistrut beam clamp | No. | 44
| AE1 Issue 28 | Terminal Range Support
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 3
|  | - Unistrut 41 x 41 mm | m | 9
|  | - Unistrut beam clamp | No. | 6
Total Carried forward to Summary Page

## Feltex AE4
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
FELTEX FACTORY AE4
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be keyed alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK3521 | No. | 1
|  | ESFR VK3502 | No. | 1
Sprinklers
Spare Sprinklers:
|  | ESFR VK3521 Pendant Spray 68 Deg C | No. | 54
|  | ESFR VK3502 Upright Spray 68 Deg C | No. | 24
| 7,7; 8; 10; 14 & 20 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New bypass Valve 2 - 100mm Diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble & modify existing valves (100 diam . | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
| 7.14 | Flow Measuring Device
The flow apparatus must be sized to suit the flow requirements on the block plan
|  | - Install flow meter to match K factor of installed sprinklers | No. | 1
| 7,20 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 4
|  | - 25 diam elbows | No. | 7
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
|  | - 50 diam elbows | No. | 7
| AE4 Issue 1 | New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 60
|  | - 32 mm diam pipe | m | 60
|  | - 40 mm diam pipe | m | 30
|  | - 50 mm diam pipe | m | 15
|  | - 65 mm diam pipe | m | 15
|  | - 80 mm diam pipe | m | 15
|  | - 100 mm diam pipe | m | 60
|  | - 25 mm sprinkler equal Tee | No. | 10
|  | - 32 mm sprinkler reducing Tee | No. | 10
|  | - 40 mm sprinkler reducing Tee | No. | 10
|  | - 50 mm sprinkler reducing Tee | No. | 10
|  | - 32 - 25 mm diam reducers | No. | 10
|  | - 40 - 32 mm diam reducers | No. | 10
|  | - 50 - 40 mm diam reducers | No. | 10
|  | - 65 - 50 mm diam reducers | No. | 10
|  | - 80 - 65 mm diam reducers | No. | 10
|  | - 100 - 80 mm diam reducers | No. | 10
|  | - 80 mm diam equal tee | No. | 10
|  | - 100 mm diam equal tee | No. | 10
|  | - 80 mm diam elbow | No. | 10
|  | - 100 mm diam elbow | No. | 10
|  | ESFR VK3542 Conventional Spray 141 Deg C | No. | 150
Carried forward to Next Page
Carried forward from Previous Page
| AE4 Issue 2 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 28
Total Carried forward to Summary Page

## Feltex AE6
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
FELTEX FACTORY AE6
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be keyed alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK3521 | No. | 1
|  | ESFR VK3542 | No. | 1
Sprinklers
Spare Sprinklers:
|  | ESFR VK3521 Pendant Spray 68 Deg C | No. | 54
|  | ESFR VK3542 Conventional Spray 141 Deg C | No. | 24
| 7,7; 8; 10; 14 & 20 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New bypass Valve 2 - 100mm Diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble & modify existing valves (100 diam . | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
| 7.14 | Flow Measuring Device
|  | - 50 mm pipe support | No. | 2
The flow apparatus must be sized to suit the flow requirements on the block plan
|  | - Install flow meter to match K factor of installed sprinklers | No. | 1
| 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1 & 2 | No. | 40
| 7,20 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 4
|  | - 25 diam elbows | No. | 7
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
|  | - 50 diam elbows | No. | 7
| AE6 Issue 3 | Pipe Supports
|  | The riser main must be properly supported in accordance with the rules | PC SUM |  |  |  | 21000
Total Carried forward to Summary Page

## Draeger
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDINGS |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
DRAEGER FACTORY
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 1
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK118 Standard Response | No. | 1
|  | Conventional VK354 Quick Response | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK118 Standard Response | No. | 28
|  | Conventional VK354 Quick Response | No. | 33
Total Carried forward to Summary Page

## Automould
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
Automould
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK531 | No. | 1
|  | Pendant VK302 | No. | 1
Sprinklers
Spare Sprinklers:
|  | ESFR VK531 93 Deg C | No. | 45
|  | Pendant VK302 93 Deg C | No. | 24
Carried forward to Next Page
Carried forward from Previous Page
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
| 7.12 | Pipe Supports
|  | The riser main must be properly supported in accordance with the rules | PC SUM |  |  |  | 21000
| 7,20 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 4
|  | - 25 diam elbows | No. | 7
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
|  | - 50 diam elbows | No. | 7
| 7.27 | Chains and Padlocks
|  | - light duty chain | m | 4
|  | - Padlock barrels to be keyed alike to current EL IDZ master key. | No. | 8
| Issue 1 | Terminal Range Support
1st range hangers exceed maximum distance of 2 m
|  | - install new 65 mm hangar | No. | 1
| Issue 2 | Pipe Supports
Additional hangers required for range pipes - production side between second and third sprinklers
|  | - install new 65 mm hangar | No. | 1
|  | - Unistrut 41 x 41 mm | m | 3
|  | - Unistrut beam clamp | No. | 2
| Issue 3 | Terminal Range Support
Distribution pattern of sprinkler - second sprinkler from east wall
|  | - Remove hangar and reinstall 150 mm clear of sprinkler | No. | 1
| Issue 4 | Unprotected / Exposed Pipework
|  | - 32 mm diam socket into 150 main feed | No. | 1
|  | - 32 mm diam pipe | m | 12
|  | - 32 mm diam elbow | No. | 4
|  | - Cut off sprinkler K Factor 11.2 | No. | 1
Total Carried forward to Summary Page

## Sundale
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
SUNDALE
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan, with the following information indicated: | No. | 1
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7.7 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New Bypass Valve 2 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
| 7,8 | New Fire Booster Connection Area A:
|  | - 100 diam pipe | m | 5
|  | - 100 diam elbow | No. | 3
|  | - 100 diam tee | No. | 1
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
| 7,2 | Flow Test Assembly
|  | Flow test assembly gauges do not rest at zero and must be recalibrated | No. | 2
| 7.27 | Corroded Pipe
Replace corroded pipe:
|  | - 54 mm diam pipe | m | 1
|  | - 54 mm isolating valve | No. | 2
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 1 | Pipe Supports
Distribution pattern of sprinklers affected - Dispatch area, packing area, old cheese areas (hangers)
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 9
|  | - Unistrut 41 x 41 mm | m | 27
|  | - Unistrut beam clamp | No. | 54
| Area 1 Issue 3 | Pipe Supports
Hangers have come adrift and must be refixed - Filling (Yoghurt) beneath stairs, old cheese area to their original positions.
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 2
| Area 1 Issue 4 | Corroded Pipe
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 90
|  | - 32 mm diam pipe | m | 45
|  | - 40 mm diam pipe | m | 45
|  | - 50 mm diam pipe | m | 51
|  | - 65 mm diam pipe | m | 45
|  | - 80 mm diam pipe | m | 10
|  | - 100 mm diam pipe | m | 12
|  | - 150 mm diam pipe | m | 12
|  | - 25 mm sprinkler equal Tee | No. | 70
|  | - 32 mm sprinkler reducing Tee | No. | 10
|  | - 40 mm sprinkler reducing Tee | No. | 5
|  | - 50 mm sprinkler reducing Tee | No. | 15
|  | - 32 - 25 mm diam reducers | No. | 10
|  | - 40 - 32 mm diam reducers | No. | 10
|  | - 50 - 40 mm diam reducers | No. | 10
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 1
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 54 mm socket | No. | 10
|  | ESFR VK3542 Conventional Spray 141 Deg C | No. | 57
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 6 | Pipe Supports
Terminal hangers on distribution pipes are exceeding the maximum distance of 450 mm from the end of the distribution pipe - packing area
|  | - 150 mm diam hangar, G Clamp and hanging rod. | No. | 1
| Area 1 Issue 8 | Reposition Sprinklers
Sprinkler spaced to close to a wall or partitioning - the minimum distance a sprinkler may be from a wall or partition shall not be less than 150 mm - redundant cheese cold storage room
|  | - 32 mm diam pipe | No. | 6
|  | - 30 to 32 mm connector | No. | 6
|  | - Dissasemmble 3m section of 32 mm range pipe, Tee to Tee. | No. | 6
| Area 2 Issue 3 | Additional Sprinkler Install
Sprinklers are out of effective working distance - dispatch office
|  | - 32 mm diam sprinkler reducing tee to 25 mm | No. | 1
|  | - Gl5651 Pendent Sprinkler | No. | 1
|  | - Dissasemmble 3m section of 32 mm range pipe, Tee to Tee. | No. | 1
| Area 2 Issue 4 | Swop Sprinkler
Upright spray pattern sprinklers installed in the pendent position - 1st floor storage level all sprinklers at ceiling
|  | - Gl5651 Pendent Sprinkler | No. | 1
| Area 3 Issue 1 | Pipe Supports
Terminal hangers on distribution pipes are exceeding the maximum distance of 450 mm from the end of the distribution pipe - packing area
|  | - 100 mm diam hangar, G Clamp and hanging rod. | No. | 1
|  | - Unistrut 41 x 41 mm | m | 3
|  | - Unistrut beam clamp | No. | 2
Total Carried forward to Summary Page

## C2 Yanfeng
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
C2 Yangfeng
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 6
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK510 | No. | 1
|  | Pendant VK102 | No. | 1
|  | Conventional VK354 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Upright VK100 141 deg C | No. | 36
|  | Conventional VK102 68 Deg C | No. | 54
|  | Conventional VK102 93 Deg C | No. | 36
|  | Pendant VK118 141 Deg C | No. | 36
|  | Conventional VK354 93 Deg C | No. | 36
|  | ESFR VK510 74 Deg C | No. | 35
| Area 1 Issue 1 | Terminal Range Support
Distribution pattern of sprinklers affected - Cleaning bay south west corner (terminal hangers)
|  | - Remove hangar and reinstall 150 mm clear of sprinkler | No. | 3
|  | - Unistrut 41 x 41 mm | m | 9
|  | - Unistrut beam clamp | No. | 6
| Area 1 Issue 3 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 75
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 4 | Pipe Supports
Additional range pipe hangers must be installed to support the range pipe lengths between adjacent sprinklers - Beneath mezzanine and at roof
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 49
|  | - Unistrut 41 x 41 mm | m | 147
|  | - Unistrut beam clamp | No. | 98
Total Carried forward to Summary Page

## AW4 Molan Pino
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
AW4 Molan Pino
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 1
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK510 | No. | 1
Sprinklers
Spare Sprinklers:
|  | ESFR VK510 | No. | 30
| 7,7 | New ByPass
|  | - 150 diam pipe | m | 1
|  | - 150 diam elbows | No. | 2
|  | - 150 diam stop valves (Nibco) | No. | 2
|  | - 150 diam non return valve | No. | 1
|  | - 150 diam Flanged Tee | No. | 2
Carried forward to Next Page
Carried forward from Previous Page
| Area 3 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 4.5
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 0
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 0
|  | - 100 mm diam ebows | No. | 0
|  | - 40 mm socket | No. | 3
|  | ESFR VK510 | No. | 9
Total Carried forward to Summary Page

## AW6 Syncro
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
AW6 Syncro
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 1
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | ESFR VK503 | No. | 1
Sprinklers
Spare Sprinklers:
|  | ESFR VK510 | No. | 30
| Area 1 issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 113
Carried forward to Next Page
Carried forward from Previous Page
| Area 3 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 4.5
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 0
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 0
|  | - 100 mm diam ebows | No. | 0
|  | - 40 mm socket | No. | 3
|  | ESFR VK510 | No. | 9
Total Carried forward to Summary Page

## AW8 AW9
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
AW8 AW9 Yanfeng
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 1
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Pendant VK102 | No. | 1
|  | ESFR VK503 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Pendant VK102 | No. | 24
|  | ESFR VK510 | No. | 30
| Area 1 issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 113
| 7,7 | New ByPass
Valve 1:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Valve 2:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Total Carried forward to Summary Page

## BW1 BW2
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
BW1 BW2
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No.
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Pendant VK102 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Pendant VK102 | No. | 54
Carried forward to Next Page
Carried forward from Previous Page
| 7,7; 8; 10; 14 & 20 | Sprinklers Valves
New Manifold:
- 200 diam pipe manifold 3m in length
- 2x 150 diam supply flanges
- 1x 100 diam supply flange
|  | New Valve 1 - 200mm diam | No. | 1
- 200 diam pipe
- 200 diam elbows
- 200 diam stop valves (Nibco)
- 200 diam non return valve
- 200 diam Flanged Tee
- 25 diam nipple for flow switch
- 25 diam test pipe to drain pt 1m external of chamber + flow meter.
- 50 diam drain pipe to drain pt 1m external of chamber.
- 50 diam flushing connection
|  | New Valve 2: | No. | 1
- 200 diam pipe
- 200 diam elbows
- 200 diam stop valves (Nibco)
- 200 diam non return valve
- 200 diam Flanged Tee
- 25 diam nipple for flow switch
- 25 diam test pipe to drain pt 1m external of chamber + flow meter.
- 50 diam drain pipe to drain pt 1m external of chamber.
- 50 diam flushing connection
|  | New Valve 3: | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
- 25 diam nipple for flow switch
- 25 diam test pipe to drain pt 1m external of chamber + flow meter.
- 50 diam drain pipe to drain pt 1m external of chamber.
- 50 diam flushing connection
New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
Total Carried forward to Summary Page

## BW3
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
BW3
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No.
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Pendant VK102 | No. | 1
|  | ESFR VK503 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Pendant VK102 | No. | 24
|  | ESFR VK503 | No. | 45
| 7.25 | Alarm Motor & Gong
|  | - Replace alarm motor and gong | No. | 2
| 7.26 | Chains and Padlocks
|  | - light duty chain | m | 4
|  | - Padlock barrels to be keyed alike to current EL IDZ master key. | No. | 8
Total Carried forward to Summary Page

## CW1
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
CW1
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 1
|  | Large - 36 heads 15 mm Diam | No.
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK310 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK310 | No. | 36
| Area 3 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 18
|  | - 40 mm diam pipe | m | 18
|  | - 50 mm diam pipe | m | 18
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 6
|  | - 40 mm sprinkler reducing Tee | No. | 6
|  | - 50 mm sprinkler reducing Tee | No. | 6
|  | - 32 - 25 mm diam reducers | No. | 0
|  | - 40 - 32 mm diam reducers | No. | 6
|  | - 50 - 40 mm diam reducers | No. | 6
|  | - 65 - 50 mm diam reducers | No. | 6
|  | - 80 - 65 mm diam reducers | No. | 1
|  | - 100 - 80 mm diam reducers | No. | 1
|  | - 80 mm diam equal tee | No. | 1
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 50 mm socket | No. | 6
|  | ESFR VK310 | No. | 18
Total Carried forward to Summary Page

## CE1
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
CE1
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 6
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK118 | No. | 1
|  | Conventional VK310 | No. | 1
|  | ESFR VK510 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK118 68 DegC | No. | 54
|  | Pendant VK302 68 Deg C | No. | 54
|  | Pendant VK302 141 Deg C | No. | 54
|  | Conventional VK310 93 Deg C | No. | 54
|  | Conventional VK310 141 Deg C | No. | 54
|  | ESFR VK510 | No. | 45
| Area 1 Issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 40
Carried forward to Next Page
Carried forward from Previous Page
| Area 2 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 1280
|  | - 40 mm diam pipe | m | 60
|  | - 50 mm diam pipe | m | 60
|  | - 65 mm diam pipe | m | 0
|  | - 80 mm diam pipe | m | 0
|  | - 100 mm diam pipe | m | 60
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 40
|  | - 40 mm sprinkler reducing Tee | No. | 20
|  | - 50 mm sprinkler reducing Tee | No. | 20
|  | - 32 - 25 mm diam reducers | No. | 0
|  | - 40 - 32 mm diam reducers | No. | 20
|  | - 50 - 40 mm diam reducers | No. | 20
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 1
|  | - 80 mm diam elbows | No. | 0
|  | - 100 mm diam ebows | No. | 1
|  | - 50 mm socket | No. | 20
|  | ESFR VK510 | No. | 80
Total Carried forward to Summary Page

## BE5
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
BE5
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK310 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK310 | No. | 36
| 7.2 | Drain & Test Pipes
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 4
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 9
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 0
|  | - 50 mm diam pipe | m | 0
|  | - 65 mm diam pipe | m | 9
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 3
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 3
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 65 mm socket | No. | 3
|  | ESFR VK310 | No. | 80
| Area 1 issue 2 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 96
| Area 1 issue 3 | Pipe Supports
Additional range pipe hangers must be installed to support the range pipe lengths between adjacent sprinklers - Beneath mezzanine and at roof
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 1
|  | - Unistrut 41 x 41 mm | m | 3
|  | - Unistrut beam clamp | No. | 2
Total Carried forward to Summary Page

## BE4
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
BE4
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 1
|  | Large - 36 heads 15 mm Diam | No. | 0
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK310 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK310 | No. | 36
| 7,8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 21
|  | - 32 mm diam pipe | m | 42
|  | - 40 mm diam pipe | m | 14
|  | - 50 mm diam pipe | m | 0
|  | - 65 mm diam pipe | m | 0
|  | - 80 mm diam pipe | m | 0
|  | - 100 mm diam pipe | m | 40
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 14
|  | - 32 mm sprinkler reducing Tee | No. | 14
|  | - 40 mm sprinkler reducing Tee | No. | 14
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 14
|  | - 40 - 32 mm diam reducers | No. | 14
|  | - 50 - 40 mm diam reducers | No. | 14
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 1
|  | - 80 mm diam elbows | No. | 0
|  | - 100 mm diam ebows | No. | 1
|  | - 40 mm socket | No. | 14
|  | ESFR VK310 | No. | 26
| Area 2 issue 2 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 40
Total Carried forward to Summary Page

## BE2
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
BE2
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 4
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK310 | No. | 1
|  | ESFR VK510 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK118 | No. | 24
|  | Pendant VK302 | No. | 54
|  | Conventional VK310 | No. | 54
|  | ESFR VK510 | No. | 45
| 7,7 | New ByPass
Valve 1:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Carried forward to Next Page
Carried forward from Previous Page
Valve 2:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Valve 3:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Valve 4:
|  | - 150 diam pipe | m | 1
|  | - 150 diam elbows | No. | 2
|  | - 150 diam stop valves (Nibco) | No. | 2
|  | - 150 diam non return valve | No. | 1
|  | - 150 diam Flanged Tee | No. | 2
| 7,8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 9
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 0
|  | - 50 mm diam pipe | m | 0
|  | - 65 mm diam pipe | m | 9
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 3
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 3
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 65 mm socket | No. | 3
|  | ESFR VK310 | No. | 80
| Area 2 Issue 3 | Pipe Supports
Hangers have come adrift and must be refixed to their original positions - 6th array from north wall
|  | - Reinstall 65 mm Hangar | No. | 1
Total Carried forward to Summary Page

## Frotek
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
FROTEK
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK310 | No. | 1
|  | ESFR VK510 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK310 | No. | 54
|  | ESFR VK510 | No. | 45
| 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1; 2 & 3 | No. | 41
| 7.27 | Gauge Cocks
|  | Gauge cocks without bleeds must be replaced. | No. | 4
Carried forward to Next Page
Carried forward from Previous Page
| Area 2 Issue 1 | New range pipe + sprinklers
|  | - 40 mm diam pipe | m | 3
|  | - 40 mm diam sprinkler reducing tee to 25 mm | No. | 9
|  | - 40 mm diam elbows | No. | 2
|  | - 40 mm sockets | No. | 9
|  | - 80 mm diam pipe | m | 18
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 6
|  | - 40 mm diam pipe | m | 6
|  | - 50 mm diam pipe | m | 12
|  | - 65 mm diam pipe | m | 18
|  | - 80 mm diam pipe | m | 18
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 3
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 3
|  | - 65 - 50 mm diam reducers | No. | 1
|  | - 80 - 65 mm diam reducers | No. | 1
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 2
|  | - 100 mm diam ebows | No. | 0
|  | - 65 mm socket | No. | 3
|  | ESFR VK510 | No. | 17
Total Carried forward to Summary Page

## Tugger
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
TUGGER ROUTE
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 1
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK310 | No. | 1
Sprinklers
Spare Sprinklers:
|  | Conventional VK310 | No. | 36
| 7,7 | New ByPass
Valve 1:
|  | - 150 diam pipe | m | 1
|  | - 150 diam elbows | No. | 2
|  | - 150 diam stop valves (Nibco) | No. | 2
|  | - 150 diam non return valve | No. | 1
|  | - 150 diam Flanged Tee | No. | 2
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 1 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 93
|  | - Unistrut 41 x 41 mm | m | 279
|  | - Unistrut beam clamp | No. | 186
| Area 1 Issue 2 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 93
|  | - Unistrut 41 x 41 mm | m | 279
|  | - Unistrut beam clamp | No. | 186
| Area 1 Issue 3 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 102
| Area 1 Issue 4 | Replace Sprinklers
|  | Pendent spray pattern sprinklers installed in the upright position. | No. | 80
Total Carried forward to Summary Page

## D Fence
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
D FENCE
Automatic Sprinkler System
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 2
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | HV-A8 | No. | 1
|  | ESFR VK506 | No. | 1
|  | ESFR VK510 | No. | 1
Sprinklers
Spare Sprinklers:
|  | HV-A8 | No. | 24
|  | ESFR VK506 | No. | 30
|  | ESFR VK510 | No. | 30
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
| 7.2 | Drain & Test Pipes
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 12
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 12
Carried forward to Next Page
Carried forward from Previous Page
| Area 1 Issue 1 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 3
|  | - Unistrut 41 x 41 mm | m | 9
|  | - Unistrut beam clamp | No. | 6
Total Carried forward to Summary Page

## EW1
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
EW1
Automatic Sprinkler System
| 7,4 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
| 7,8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
| 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1; 2 & 3 | No. | 56
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 3
|  | Large - 36 heads 15 mm Diam | No. | 2
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Upright VK300 | No. | 1
|  | Conventional VK302 | No. | 1
|  | ESFR VK510 | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
Sprinklers
Spare Sprinklers:
|  | Upright VK300 | No. | 54
|  | Conventional VK302 | No. | 54
|  | Conventional VK310 | No. | 54
|  | ESFR VK510 | No. | 45
| Area 1 Issue 1 | Swop Sprinkler
Upright spray pattern sprinklers installed in the pendent position - 1st floor storage level all sprinklers at ceiling
|  | - Gl5651 Pendent Sprinkler | No. | 1
| Area 1 Issue 2 | Additional Sprinkler Install
Sprinklers are out of effective working distance - first aid room
|  | - 32 mm diam sprinkler reducing tee to 25 mm | No. | 1
|  | - Gl5651 Pendent Sprinkler | No. | 1
|  | - Dissasemmble 3m section of 32 mm range pipe, Tee to Tee. | No. | 1
| Area 1 Issue 3 | Additional Sprinkler Install
Sprinklers are out of effective working distance - first aid room
|  | - 32 mm diam sprinkler reducing tee to 25 mm | No. | 1
|  | - Gl5651 Pendent Sprinkler | No. | 1
|  | - Dissasemmble 3m section of 32 mm range pipe, Tee to Tee. | No. | 1
| Area 2 Issue 3 | Sprinkler Spacing
Sprinklers are incorrectly spaced from the draft curtain at roof level
|  | - move 80 mm ranges in gridded system away from fraft curtain, 9 sprinklers per range = approximately 18 m per range. | No. | 8
| Area 3 Issue 1 | Additional Sprinkler Install
|  | Reinstante plugged sprinkler, south side stairs. VK310 | No. | 1
Total Carried forward to Summary Page

## FE1
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
FE1
Automatic Sprinkler System
| 7,8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
| 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
| 7,6,2 | Sprinkler Cabinet
Wall mounted, colour RED, c/w lockable latches, barrels to be key alike to current EL IDZ master key.
|  | Large - 36 heads 25 mm Diam | No. | 2
|  | Large - 36 heads 15 mm Diam | No. | 2
| 7,6,2 | Sprinkler spanner
Sprinkler spanner to suit sprinkler:
|  | Conventional VK118 | No. | 1
|  | Upright VK302 | No. | 1
|  | Conventional VK302 | No. | 1
|  | ESFR VK510 | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
Sprinklers
Spare Sprinklers:
|  | Upright VK118 | No. | 54
|  | Conventional VK302 | No. | 54
|  | Conventional VK310 | No. | 54
|  | ESFR VK510 | No. | 45
| Area 1 Issue 1 | Pipe Supports
Terminal hangers on distribution pipes are exceeding the maximum distance of 450 mm from the end of the distribution pipe - packing area
|  | - 65 mm diam hangar, G Clamp and hanging rod. | No. | 23
| Area 1 Issue 2 | Vertical supports for North Wall
Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser
|  | - 40 mm pipe support | No. | 3
| Area 1 Issue 3 | Vertical supports for External West Canopy
The sprinkler pipe work must be correctly supported.
|  | - 40 mm pipe support | No. | 2
Total Carried forward to Summary Page

## Summary
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
PROVISIONAL SCHEDULE OF QUANTITIES
FINAL SUMMARY PAGE
Item No. | Description | Total Amount
1 | SCHEDULE NO 1: PRELIMINARY & GENERAL
2 | Feltex AE 1
3 | Feltex AE 4
4 | Feltex AE 6
5 | Draeger
6 | Automould
7 | Sundale
8 | C2 Yanfeng
9 | AW 4 Molan Pino
10 | AW6 MC Syncro
11 | AW8 & AW 9
12 | BW1 & BW2
13 | BW 3
14 | CW 1
15 | CE 1
16 | BE 5
17 | BE 4
18 | BE 2
19 | Frotek
20 | Tugger
21 | D Fence
22 | EW 1
23 | FE 1
24 | PC SUM - UPGRADE OF SPRINKLER MAIN | 500000
Total carried to Form of Offer and Acceptance (Ex VAT)