## 1 P & G
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
SCHEDULE NO 1: PRELIMINARY & GENERAL
ITEM
NO | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
TITY
1 | CONTRACTUAL CONDITIONS
1.1 | Compliance with General Conditions of Contract : Insurances, Sureties, etc as outlined in the Principal Contractor's Preliminaries.
1.2 | Establish on Site and provision of buildings and storage facilities including de-establishment of site, cleaning and tidying up after completion of contract
| Fixed | Item | 1
| Value Related | Item | 1
| Time Related | Item | 1
1.3 | Tools and equipment, Communication, transport.
| Fixed | Item | 1
| Value Related | Item | 1
| Time Related | Item | 1
1.4 | Contract Management, Company overheads and supervision of the Works including attendance of site meetings (2 per month)
| Fixed | Item | 1
| Value Related | Item | 1
| Time Related | Item | 1
| Attendance at site meetings | Sum | 1
1.5 | Provision of all drawings and manuals as specified including As-Installed drawings | Item | 1
1.6 | Liaison with Local Supply Authority, compliance with OSH Act, Local By-laws and any other statutory regulations | Item | 1
1.7 | DAYWORK SCHEDULE
Personnel
| Coded welder | hr |  |  | Rate only
| Registered electrician | hr |  |  | N/A
| Registered HVAC technician | hr |  |  | N/A
| Apprentice | hr |  |  | Rate only
| Labourer | hr |  |  | Rate only
Carried forward
SCHEDULE NO 1: PRELIMINARY & GENERAL
ITEM | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
NO |  |  | TITY
Brought forward
1.9 | GUARANTEE
| 12 month guarantee of plant and | Sum | 1
equipment as specified
Allowance for servicing the plant
during the guarantee period
| Monthly service calls to check plant | No | 8
operation, clean filters, etc
| 3 monthly minor service as specified | No | 3
| Annual major service at the end of | No | 1
the guarantee period
1.10 | Additional Tests
Allow for aditional tests as direct by
| the Consulting Engineer | PC SUM |  |  | 150000
1.11 | Additional items
Any additional items the contractor
wishes to allow for:
(Specify)
TOTAL SCHEDULE NO 1 - CARRIED TO SUMMARY

## 2 Estate Pump House
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9004 | ESTATE PUMP HOUSE
Automatic Sprinkler System
1.1 | 6,1,8 | Block Plan
|  | Provide new block plan, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
1.2 |  | Flange Bolts
Flow Meter Flanges Short Bolted
1,2,1 | 5.1 | Bolts for these flanges be removed and replaced with the correctly sized bolts so as to ensure that at least two full thread pitches past the chamfer protrude beyond the nut. | No. | 15
Various Flanges Short Bolted
1,2,2 | 6,2,8 | Bolts for these flanges be removed and replaced with the correctly sized bolts so as to ensure that at least two full thread pitches past the chamfer protrude beyond the nut. | No. | 60
1.3 | 6,5,30 | Glands Condition
|  | Replace pump 1x gland packing | PC SUM | 1 |  |  | 25000
1.4 | 6,11,1 | Power Failure - Alarm Bell
|  | Electrical Isolator failed, replace. | No. | 1
Total Carried forward to Summary Page

## 3 AE8
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC10603 | AE8
Automatic Sprinkler System
2.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
2.2 | 7.16 | Pressure Guage Cocks
|  | Replace pressure gauge isolating gauge cock with bleed outlet to confirm gauge operation back to zero and enable each pressure gauge to be readily removed without interruption of the installation water supplies. | No. | 1
2.3 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 150 mm diam Valve | No. | 40
2.4 | 7.27 | Chains and Padlocks
- light duty chain
|  | - Padlock barrels to be keyed alike to current EL IDZ master key. | No. | 1
2.5 |  | Pipe Supports
| 9 - Issue 1 | Belt-to-belt hangers must be removed and the pipe work correctly supported. | No. | 2
| 9 - Issue 2 | Hangers have come adrift and must be re-fixed to their original positions. | No. | 1
2.6 | 9 - Issue 3 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | All sprinklers located beneath open celled floors or stairwells and translucent sheeting must have approved water shields fitted above the sprinklers. | No. | 48
Total Carried forward to Summary Page

## 4 Bushveld Energy
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9855 | BUSHVELD ENERGY
Automatic Sprinkler System
3.1 | 7,4,2 | Block Plan
Provide Updated block plan, with the following information indicated:
The storage section on the left of the building has a higher design density. This must be indicated on the block plan.
Block Plan
|  | Provide new block plan, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
3.2 | 7.23 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
Total Carried forward to Summary Page

## 5 CE1 L&W
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8479 | CE1 LINDE & WIEMANN
Automatic Sprinkler System
4.1 | 7.5 | Sprinkler Valve Instruction Chart
|  | A weatherproof valve instruction chart that relates specifically to the control valve assembly installed, (not a generic instruction chart) shall be mounted on a wall within the control valve cabinet or if the valves are internally located, as close to these as possible | No. | 1
4.2 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
4.3 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 150 mm diam Valve | No. | 60
4.4 |  | Flow Meter
|  | Flow meter valve 45 gauge & pipework to be replaced. | No. | 1
4.5 | 9 - Area 1 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work and must be rectified. | PC SUM | 1 |  |  | 5000
4.6 | 9 - Area 1 Issue 3 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | All sprinklers located beneath open celled floors or stairwells and translucent sheeting must have approved water shields fitted above the sprinklers. | No. | 72
Total Carried forward to Summary Page

## 6 BE5 DSV
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8480 | BE5 DSV
Automatic Sprinkler System
5.1 | 7.5 | Sprinkler Valve Instruction Chart
|  | A weatherproof valve instruction chart that relates specifically to the control valve assembly installed, (not a generic instruction chart) shall be mounted on a wall within the control valve cabinet or if the valves are internally located, as close to these as possible | No. | 1
5.2 | 7.7 | Sprinklers Valves
|  | New bypass Valve 2 - 150mm Diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tee
|  | New bypass Valve 2 - 150mm Diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tee
|  | Labour to disassemble valves, modify existing feed main. | No. | 2
5.3 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
5.4 | 7.12 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 3
5.5 | 9 - Area 1 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work and must be rectified. | PC SUM | 1 |  |  | 5000
Carried forward to Next Page
Carried forward from Previous Page
5.5 | Area 1 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 9
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 0
|  | - 50 mm diam pipe | m | 0
|  | - 65 mm diam pipe | m | 9
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 3
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 3
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 65 mm socket | No. | 3
|  | Sprinkler Factor K8 | No. | 80
5.6 | Area 2 issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 96
5.7 | Area 1 issue 3 | Pipe Supports
|  | Pipe work must be supported independently from the composite panel, and the dry dropper must not be attached to the fabric of the cold room with mastic or insulating material that permanently bonds the dropper to the refrigerated structure. | PC Sum | 1 |  |  | 20000
Total Carried forward to Summary Page

## 7 Yakeni
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8029 | YAKENI
Automatic Sprinkler System
6.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
6.2 | 7.14 | Flow Test Arrangement
|  | Reroute flow test piping | PC SUM | 1 |  |  | 50000
6.3 | 7.2 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 4
|  | - 25 diam elbows | No. | 7
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
|  | - 50 diam elbows | No. | 7
6.4 | 7.27 | Flange Bolts
Incorrect Bolt Sizes
|  | Replace bolts to 150 mm diam Valve | No. | 24
6.5 | 9 - Area 1 Issue 1 | Sprinkler remote test valves
|  | A sprinkler remote test valve must be installed with a location plate fixed to the wall adjacent to it. The valves must be secured in the closed position by means of a light chain and/or padlock. | PC SUM | 1 |  |  | 8000
6.6 | 9 - Area 1 Issue 2 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 2
6.7 | 9 - Area 3 Issue 2 | Protective Cover
|  | Remove protective cover form sprinkler | No. | 1
6.8 | 9 - Area 3 Issue 3 | Dropped Sprinkler
|  | Sprinklers must be re-fixed to their original intended operating position | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
6.9 | 9 - Area 3 Issue 4 | Sprinkler Spacing
Sprinklers spaced too far apart. (The protection must be revised in this area so that the following spacing is achieved: Sprinklers must be spaced a maximum of 4,0 meters apart. Each sprinkler must cover a maximum area of 12 m²)
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 15
|  | - 25 mm diam elbow | m | 2
|  | - 25 mm diam socket | m | 3
|  | - Sprinkler Factor K8 | No. | 3
6.1 | 9 - Area 4 Issue 2 | Terminal Range Support
Terminal hangers on distribution pipes are exceeding the maximum distance of 450 mm from the end of the distribution pipe
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 3
|  | - Angle iron brackets 100x65x7 mm | m | 9
|  | - Perlin clamp | No. | 6
6.11 | 9 - Area 4 Issue 3 | Sprinkler
|  | Pendent spray pattern sprinklers installed in the upright position. | No. | 1
6.12 | 9 - Area 4 Issue 5 | Pipe Supports
|  | Belt-to-belt hangers must be removed and the pipe work correctly supported. | No. | 4
Total Carried forward to Summary Page

## 8 GW1 Valeo
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9029 | GW1 VALEO
Automatic Sprinkler System
7.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
7.2 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
7.3 | 9 - Area 1 Issue 1 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 16
|  | - Angle iron brackets 100x65x7 mm | m | 48
|  | - Perlin clamp | No. | 32
7.4 | 9 - Area 1 Issue 2 | Riser Mains Support
Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser
|  | The riser main must be properly supported in accordance with the rules | No. | 3
7.5 | 9 - Area 1 Issue 3 | Terminal Range Support
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 16
|  | - Angle iron brackets 100x65x7 mm | m | 48
|  | - Perlin clamp | No. | 32
Carried forward to Next Page
Carried forward from Previous Page
7.6 | 9 - Area 2 Issue 1 | Riser Mains Support
Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser
|  | The riser main must be properly supported in accordance with the rules | No. | 8
Total Carried forward to Summary Page

## 9 GE1 Auria
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9084 | GE1 AURIA
Automatic Sprinkler System
8.1 | 7.8 | Sprinklers Valves
New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
8.2 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 2
|  | - 25 mm test pipe | m | 8
|  | - 25 mm elbows | m | 14
8.3 | 7.12 | Pipe Supports
|  | The riser main must be properly supported in accordance with the rules | No. | 4
8.4 | 7.14 | Flow Test Arrangement
|  | New Flow test arrangement to be installed | PC SUM | 1 |  |  | 50000
8.5 | 7.24 | Valve 3 Yearly Overhaul
|  | The installation control valves must be overhauled three years after date of installation by an ASIB approved and registered installer, and once every 3 years thereafter. An ASIB valve overhaul date tag must be attached to the valve set after completion of the overhaul. | No. | 2
8.6 | 7.27 | Chains and Padlocks
- light duty chain
|  | - Padlock barrels to be keyed alike to current EL IDZ master key. | No. | 2
Carried forward to Next Page
Carried forward from Previous Page
8.7 | 9 - Area 1 Issue 1 | Dropped Sprinkler
|  | Sprinklers must be re-fixed to their original intended operating position | No. | 1
8.8 | 9 - Area 1 Issue 2 | Sprinkler Spacing
Sprinkler protection must be extended in order to provide correct coverage.
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 15
|  | - 25 mm diam elbow | m | 2
|  | - 25 mm diam socket | m | 3
|  | - Sprinkler Factor K8 | No. | 3
8.9 | 9 - Area 2 Issue 3 | Partial Protection
|  | Plant room | PC SUM | 1 |  |  | 20000
8.1 | 9 - Area 2 Issue 4 | Mains Feed Support
|  | The riser main must be properly supported in accordance with the rules | No. | 8
Total Carried forward to Summary Page

## 10 HW1 EBOR
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9262 | HW1 EBOR
Automatic Sprinkler System
9.1 | 7.5 | Sprinkler Valve Instruction Chart
|  | A weatherproof valve instruction chart that relates specifically to the control valve assembly installed, (not a generic instruction chart) shall be mounted on a wall within the control valve cabinet or if the valves are internally located, as close to these as possible | No. | 1
9.2 | 7.8 | Sprinklers Valves
9,2,1 |  | New Bypass Valve 1 - 100mm diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tees
9,2,2 |  | New Bypass Valve 2 - 200mm diam | No. | 1
- 200 diam pipe
- 200 diam elbows
- 200 diam stop valves (Nibco)
- 200 diam non return valve
- 200 diam Flanged Tees
9,2,3 |  | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
9.3 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 2
|  | - 25 mm test pipe | m | 8
|  | - 25 mm elbows | m | 14
9.4 | 7.12 | Pipe Supports
|  | The riser main must be properly supported in accordance with the rules | No. | 4
9.5 | 7.14 | Flow Test Arrangement
|  | New Flow test arrangement to be installed | PC SUM | 1 |  |  | 50000
Carried forward to Next Page
Carried forward from Previous Page
9.6 | 7.15 | Pressure Gauges
No trunk main gauge installed
|  | Install correct pressure gauge to trunk main | No. | 1
9.7 | 7.25 | Alarm Motor & Gong
|  | Replace alarm motor and gong | No. | 1
9.8 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
9.1 | 9 - Area 1 Issue 1 | Sprinkler Spacing
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 15
|  | - 25 mm diam elbow | m | 2
|  | - 25 mm diam socket | m | 3
|  | - Sprinkler Factor K8 | No. | 3
9.11 | 9 - Area 2 Issue 2 | Mains Feed Support
Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser
|  | The riser main must be properly supported in accordance with the rules | No. | 8
9.12 | 9 - Area 2 Issue 3 | Terminal Range Support
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 30
|  | - Angle iron brackets 100x65x7 mm | m | 90
|  | - Perlin clamp | No. | 60
9.13 | 9 - Area 2 Issue 4 | Distribution Pattern
|  | Distribution pattern of sprinklers affected | No. | 1
9.14 | 9 - Area 2 Issue 5 | Exposed / unprotected pipe work
|  | Sprinkler pipe work passing through a sprinkler protected area. | PC SUM | 1 |  |  | 100000
9.15 | 9 - Area 3 Issue 3 | Distribution Main Support
|  | The distribution main must be properly supported in accordance with the rules | No. | 8
Total Carried forward to Summary Page

## 11 HE1 POLYTECH
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9263 | HE1 POLYTECH
Automatic Sprinkler System
10.1 | 7.8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
10.2 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 2
|  | - 25 mm test pipe | m | 8
|  | - 25 mm elbows | m | 14
10.3 | 7.14 | Flow Test Arrangement
|  | New Flow test arrangement to be installed | PC SUM | 1 |  |  | 50000
10.4 | 7.2 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 8
|  | - 25 diam elbows | No. | 14
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 8
|  | - 50 diam elbows | No. | 14
10.5 | 7.24 | Valve 3 Yearly Overhaul
|  | The installation control valves must be overhauled three years after date of installation by an ASIB approved and registered installer, and once every 3 years thereafter. An ASIB valve overhaul date tag must be attached to the valve set after completion of the overhaul. | No. | 2
10.5 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
10.5 | 9 - Area 1 Issue 1 | Riser Supports
|  | The risers to roof monitors must be properly supported in accordance with the rules | No. | 18
10.6 | 9 - Area 1 Issue 2 | Range Supports
|  | Belt-to-belt hangers must be removed and the pipe work correctly supported | No. | 1
10.7 | 9 - Area 2 Issue 1 | Exposed / unprotected pipe work
|  | Sprinkler pipe work passing through a sprinkler protected area. | PC SUM | 1 |  |  | 100000
Total Carried forward to Summary Page

## 12 HS1
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9499 | HS1
Automatic Sprinkler System
11.1 | 7.8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
11.2 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 2
|  | - 25 mm test pipe | m | 8
|  | - 25 mm elbows | m | 14
11.3 | 7.12 | Mains Feed Support
|  | The riser main must be properly supported in accordance with the rules | No. | 8
11.4 | 7.2 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 8
|  | - 25 diam elbows | No. | 14
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 8
|  | - 50 diam elbows | No. | 14
11.5 | 7.24 | Valve 3 Yearly Overhaul
|  | The installation control valves must be overhauled three years after date of installation by an ASIB approved and registered installer, and once every 3 years thereafter. An ASIB valve overhaul date tag must be attached to the valve set after completion of the overhaul. | No. | 2
11.6 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
11.7 | 9 - Area 1 Issue 1 | Terminal Range Support
Terminal hangers on distribution pipes are exceeding the maximum distance of 450 mm from the end of the distribution pipe
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 30
|  | - Angle iron brackets 100x65x7 mm | m | 90
|  | - Perlin clamp | No. | 60
11.8 | 9 - Area 1 Issue 3 | Exposed / unprotected pipe work
|  | Sprinkler pipe work passing through a sprinkler protected area. | PC SUM | 1 |  |  | 100000
11.9 | 9 - Area 1 Issue 4 | Mains Feed Support
Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser
|  | The riser main must be properly supported in accordance with the rules | No. | 15
11.1 | 9 - Area 2 Issue 3 | Terminal Range Support
Terminal hangers on distribution pipes are exceeding the maximum distance of 450 mm from the end of the distribution pipe
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 2
|  | - Angle iron brackets 100x65x7 mm | m | 6
|  | - Perlin clamp | No. | 4
Total Carried forward to Summary Page

## 13 CW1 AIC
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8478 | CW1 AIC
Automatic Sprinkler System
12.1 | 7,4,2 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
12.2 | 7.8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
12.3 | 7.11 | Manifold Correctly Supported
|  | New Manifold supports | No. | 4
12.4 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1; 2 & 3 | No. | 48
Carried forward to Next Page
Carried forward from Previous Page
12.5 | 9 - Area 3 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 18
|  | - 40 mm diam pipe | m | 18
|  | - 50 mm diam pipe | m | 18
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 6
|  | - 40 mm sprinkler reducing Tee | No. | 6
|  | - 50 mm sprinkler reducing Tee | No. | 6
|  | - 32 - 25 mm diam reducers | No. | 0
|  | - 40 - 32 mm diam reducers | No. | 6
|  | - 50 - 40 mm diam reducers | No. | 6
|  | - 65 - 50 mm diam reducers | No. | 6
|  | - 80 - 65 mm diam reducers | No. | 1
|  | - 100 - 80 mm diam reducers | No. | 1
|  | - 80 mm diam equal tee | No. | 1
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 50 mm socket | No. | 6
|  | - Sprinkler Factor K8 | No. | 18
Total Carried forward to Summary Page

## 14 B2; 4 & 6 L&W
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8481 | B2; 4 & 6 Linde & Wiemann
Automatic Sprinkler System
13.1 | 7,4,2 | Sprinklers Valves
13,1,1 |  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
13,1,2 |  | New Bypass Valve 2 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
13,2,3 |  | New Bypass Valve 3 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
13.2 | 7.8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
13.3 | 7.11 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 9
Carried forward to Next Page
Carried forward from Previous Page
13.4 | 9 - Area 1 Issue 2 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 18
|  | - 40 mm diam pipe | m | 18
|  | - 50 mm diam pipe | m | 18
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 6
|  | - 40 mm sprinkler reducing Tee | No. | 6
|  | - 50 mm sprinkler reducing Tee | No. | 6
|  | - 32 - 25 mm diam reducers | No. | 0
|  | - 40 - 32 mm diam reducers | No. | 6
|  | - 50 - 40 mm diam reducers | No. | 6
|  | - 65 - 50 mm diam reducers | No. | 6
|  | - 80 - 65 mm diam reducers | No. | 1
|  | - 100 - 80 mm diam reducers | No. | 1
|  | - 80 mm diam equal tee | No. | 1
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 50 mm socket | No. | 6
|  | - Sprinkler Factor K8 | No. | 18
13.5 | 9 - Area 2 Issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | All sprinklers located beneath open celled floors or stairwells and translucent sheeting must have approved water shields fitted above the sprinklers. | No. | 56
Carried forward to Next Page
Carried forward from Previous Page
13.6 | 9 - Area 2 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 18
|  | - 40 mm diam pipe | m | 18
|  | - 50 mm diam pipe | m | 18
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 6
|  | - 40 mm sprinkler reducing Tee | No. | 6
|  | - 50 mm sprinkler reducing Tee | No. | 6
|  | - 32 - 25 mm diam reducers | No. | 0
|  | - 40 - 32 mm diam reducers | No. | 6
|  | - 50 - 40 mm diam reducers | No. | 6
|  | - 65 - 50 mm diam reducers | No. | 6
|  | - 80 - 65 mm diam reducers | No. | 1
|  | - 100 - 80 mm diam reducers | No. | 1
|  | - 80 mm diam equal tee | No. | 1
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 50 mm socket | No. | 6
|  | - Sprinkler Factor K8 | No. | 18
Total Carried forward to Summary Page

## 15 BE2 Martinrea SA
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8482 | BE2 Martinrea SA
Automatic Sprinkler System
14.1 | 7,4 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
14.2 | 7,7 | New ByPass
14,2,1 |  | Valve 1:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
14,2,2 |  | Valve 2:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
14,2,3 |  | Valve 3:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
14,2,4 |  | Valve 4:
|  | - 150 diam pipe | m | 1
|  | - 150 diam elbows | No. | 2
|  | - 150 diam stop valves (Nibco) | No. | 2
|  | - 150 diam non return valve | No. | 1
|  | - 150 diam Flanged Tee | No. | 2
Carried forward to Next Page
Carried forward from Previous Page
14.3 | 7,8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
14.4 | 9 - Area 1 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 9
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 0
|  | - 50 mm diam pipe | m | 0
|  | - 65 mm diam pipe | m | 9
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 3
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 3
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 1
|  | - 100 mm diam ebows | No. | 0
|  | - 65 mm socket | No. | 3
|  | - Sprinkler Factor K8 | No. | 9
14.5 | 9 - Area 2 Issue 3 | Pipe Supports
Hangers have come adrift and must be refixed to their original positions - 6th array from north wall
|  | - Reinstall 65 mm Hangar | No. | 1
14.6 | 9 - Area 2 Issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | All sprinklers located beneath open celled floors or stairwells and translucent sheeting must have approved water shields fitted above the sprinklers. | No. | 48
Total Carried forward to Summary Page

## 16 AW4 Molan Pino
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8473 | AW4 Molan Pino
Automatic Sprinkler System
15.1 | 7.3 | Fire Brigade Booster Pressure Limitation Plate
|  | Fire brigade booster pressure limitation plate must be affixed to an external wall as close to the inlets as possible | No. | 1
15.2 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
15.3 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1; 2 & 3 | No. | 8
15.5 | 9 - Area 2 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work and must be rectified. | PC SUM | 1 |  |  | 5000
Carried forward to Next Page
Carried forward from Previous Page
15.4 | 9 - Area 2 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 4.5
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 0
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 0
|  | - 100 mm diam ebows | No. | 0
|  | - 40 mm socket | No. | 3
|  | - Sprinkler Factor K36 | No. | 9
Total Carried forward to Summary Page

## 17 AW6 Molan Pino
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8474 | AW6 Molan Pino
Automatic Sprinkler System
16.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
16.2 | 7.11 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 9
16.3 | 7.17 | Flange Bolts
|  | Missing Bolts | No. | 1
16.4 | 9 Area 1 Issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | All sprinklers located beneath open celled floors or stairwells and translucent sheeting must have approved water shields fitted above the sprinklers. | No. | 48
Carried forward to Next Page
Carried forward from Previous Page
16.5 | 9 - Area 2 Issue 1 | New range pipe + sprinklers
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 9
|  | - 40 mm diam pipe | m | 4.5
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 8
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 0
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 0
|  | - 65 - 50 mm diam reducers | No. | 0
|  | - 80 - 65 mm diam reducers | No. | 0
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 0
|  | - 100 mm diam ebows | No. | 0
|  | - 40 mm socket | No. | 3
|  | - Sprinkler Factor K11,5 | No. | 9
16.6 | 9 - Area 3 Issue 1 | Escutcheon Plates
|  | The missing/damaged escutcheon plates must be replaced | No. | 1
16.7 | 9 - Area 3 Issue 2 | Sprinkler Spacing
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 15
|  | - 25 mm diam elbow | m | 2
|  | - 25 mm diam socket | m | 3
|  | - Sprinkler Factor K8 | No. | 3
Total Carried forward to Summary Page

## 18 C2 Yanfeng
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC6901 | C2 Yangfeng
Automatic Sprinkler System
17.1 | 7.5 | Sprinkler Valve Instruction Chart
|  | A weatherproof valve instruction chart that relates specifically to the control valve assembly installed, (not a generic instruction chart) shall be mounted on a wall within the control valve cabinet or if the valves are internally located, as close to these as possible | No. | 1
17.2 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
17.3 | 7.11 | Manifold Support
|  | Secure manifold to support | No. | 1
17.4 | 7.11 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 12
17.5 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1; 2 & 3 | No. | 48
17.6 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and rectified | Sum | 1
17.8 | 9 - Area 1 Issue 3 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | All sprinklers located beneath open celled floors or stairwells and translucent sheeting must have approved water shields fitted above the sprinklers. | No. | 58
Carried forward to Next Page
Carried forward from Previous Page
17.9 | 9 - Area 1 Issue 8 | Pipe Supports
Additional range pipe hangers must be installed to support the range pipe lengths between adjacent sprinklers - Beneath mezzanine and at roof
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 49
|  | - Angle iron brackets 100x65x7 mm | m | 147
|  | - Perlin clamp | No. | 98
17.1 | 9 - Area 1 Issue 14 | Riser Mains Support
Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser
|  | - 65 mm pipe hangar; G clamp and hanging rod | No. | 12
|  | - Angle iron brackets 100x65x7 mm | m | 54
|  | - Perlin clamp | No. | 24
17.11 | 9 - Area 1 Issue 17 | Range Support
|  | 1st range hangers are exceeding the maximum distance of 2,0 metres from the distribution pipe | No. | 3
Total Carried forward to Summary Page

## 19 AW8 AW9 Yanfeng
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8475 | AW8 AW9 Yanfeng
Automatic Sprinkler System
18.1 |  | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
18.2 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
18.3 | 7.11 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 9
18.4 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve | No. | 12
18.5 | 9 - Area 1 issue 1 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 113
Carried forward to Next Page
Carried forward from Previous Page
18.6 | 9 - Area 1 issue 2 | New ByPass
Valve 1:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Valve 2:
|  | - 200 diam pipe | m | 1
|  | - 200 diam elbows | No. | 2
|  | - 200 diam stop valves (Nibco) | No. | 2
|  | - 200 diam non return valve | No. | 1
|  | - 200 diam Flanged Tee | No. | 2
Total Carried forward to Summary Page

## 20 Automould
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8484 | Automould
Automatic Sprinkler System
19.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
19.2 | 7.14 | Flow Test Results
|  | Flow test arrangement is not calibrated to read the flow indicated on the blockplan. | No. | 1
19.3 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve | No. | 8
19.4 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
19.5 | 7.27 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work and must be rectified. | PC SUM | 1 |  |  | 5000
19.7 | 9 - Area 1 issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work hangers and must be rectified. | No. | 16
19.8 | 9 - Area 2 issue 1 | Pipe Supports
Additional hangers required for range pipes - production side between second and third sprinklers
|  | - install new 65 mm hangar | No. | 10
|  | - Angle iron brackets 100x65x7 mm | m | 48
|  | - Perlin clamp | No. | 20
Carried forward to Next Page
Carried forward from Previous Page
19.9 | 9 - Area 2 issue 2 | Distribution Pattern
Sprinkler spaced to close to a wall or partitioning - the minimum distance a sprinkler may be from a wall or partition shall not be less than 150 mm - redundant cheese cold storage room
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
19.1 | 9 - Area 3 issue 2 | Distribution Pattern
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
19.11 | 9 - Area 3 issue 3 | Pipe Supports
Additional hangers required for range pipes - production side between second and third sprinklers
|  | - install new 65 mm hangar | No. | 5
|  | - Angle iron brackets 100x65x7 mm | m | 33
|  | - Perlin clamp | No. | 10
19.12 | 9 - Area 3 issue 4 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 48
Total Carried forward to Summary Page

## 21 ASP Tugger
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8567 | TUGGER ROUTE
Automatic Sprinkler System
20.1 |  | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
20.2 | 7,7 | New ByPass
Valve 1:
|  | - 150 diam pipe | m | 1
|  | - 150 diam elbows | No. | 2
|  | - 150 diam stop valves (Nibco) | No. | 2
|  | - 150 diam non return valve | No. | 1
|  | - 150 diam Flanged Tee | No. | 2
20.3 | 7,8 | New Fire Booster Connection:
|  | - 100 diam pipe | m | 25
|  | - 100 diam elbow | No. | 8
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | - 150 mm to 100 mm flanged Tee | No. | 2
|  | - 100 mm to 100 mm flanged Tee | No. | 2
20.4 | 7.11 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 3
Total Carried forward to Summary Page

## 22 Sundale Cheese F
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC10601 | SUNDALE SOS CHEESE FACTORY
Automatic Sprinkler System
21.1 | 4 | Sprinkler System Design
|  | Hydraulic calculations and recommendations to satisfy finding. | Sum | 1
21.2 | 7,8 | New Fire Booster Connection
|  | - 100 diam pipe | m | 5
|  | - 100 diam elbow | No. | 3
|  | - 100 diam tee | No. | 1
|  | - 80 mm female couplings | No. | 2
|  | - 100 diam twin booster connection | No. | 1
|  | - 290 mm external signage | No. | 1
|  | Labour to disassemble valves, modify existing feed main. | No. | 1
21.3 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 1
|  | - 25 mm test pipe | m | 4
|  | - 25 mm elbows | m | 7
21.4 | 7.27 | Chains and Padlocks
- light duty chain
|  | - Padlock barrels to be keyed alike to current EL IDZ master key. | No. | 1
21.6 | 9 - Area 1 Issue 1 | Pipe Supports
|  | Terminal hangers on distribution pipes are exceeding the maximum distance of 750 mm from the end of range pipe. | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
21.7 | 9 - Area 1 Issue 3 | Pipe Supports
|  | The roof main must be properly supported in accordance with the rules | No. | 1
21.8 | 9 - Area 1 Issue 4 | Distribution
The sprinklers are spaced too far from roof/ceiling level
Sprinkler protection must be extended in order to provide correct coverage.
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 15
|  | - 25 mm diam elbow | m | 2
|  | - 25 mm diam socket | m | 3
|  | - Sprinkler Factor K8 | No. | 3
Total Carried forward to Summary Page

## 23 EW1 TIA
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8802 | EW1 TIA
Automatic Sprinkler System
22.1 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1; 2 & 3 | No. | 56
22.2 | 7.20 | Drain & Test Pipes Installed Correctly
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 4
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
22.3 | 7.25 | Alarm Motor & Gong Test
|  | Replace alarm motor and gong | No. | 1
22.4 | 9 - Area 1 Issue 1 | Swop Sprinkler
Upright spray pattern sprinklers installed in the pendent position - 1st floor storage level all sprinklers at ceiling
|  | - Sprinkler Factor K36 | No. | 1
22.5 | 9 - Area 1 Issue 2 | Additional Sprinkler Install
Sprinklers are out of effective working distance - first aid room
|  | - 32 mm diam sprinkler reducing tee to 25 mm | No. | 1
|  | - Sprinkler Factor K8 | No. | 1
|  | - Dissasemmble 3m section of 32 mm range pipe, Tee to Tee. | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
22.6 | 9 - Area 1 Issue 4 | Additional Sprinkler Install
Sprinklers are out of effective working distance - first aid room
|  | - 32 mm diam sprinkler reducing tee to 25 mm | No. | 1
|  | - Sprinkler Factor K8 | No. | 1
|  | - Dissasemmble 3m section of 32 mm range pipe, Tee to Tee. | No. | 1
22.7 | 9 - Area 2 Issue 2 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work to canopy and must be rectified. | PC SUM | 1 |  |  | 5000
22.8 | 9 - Area 4 Issue 2 | Sprinklers are Incorrectly Spaced
|  | Sprinklers are incorrectly spaced from the draft curtain at roof level. | PC SUM | 1 |  |  | 100000
22.9 | 9 - Area 4 Issue 7 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser. | No. | 1
Total Carried forward to Summary Page

## 24 AE1 Feltex
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC0191 | AE1 FELTEX FACTORY
Automatic Sprinkler System
23.1 | 4 | Sprinkler System Design
|  | The flow and pressure requirements for combined rack and roof are required. | Sum | 1
23.2 | 7.7 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New bypass Valve 2 - 100mm Diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
|  | Labour to disassemble & modify existing valves (100 diam . | No. | 1
23.3 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
23.4 | 7.2 | Sprinkler Valve Location Plate
|  | A valve location plate must be affixed on an external wall, as near to the main stop valve as possible. | No. | 1
23.5 | 7.3 | Fire Brigade Booster Pressure Limitation Plate
|  | Fire brigade booster pressure limitation plate must be affixed to an external wall as close to the inlets as possible | No. | 1
23.6 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 2
|  | - 25 mm test pipe | m | 8
|  | - 25 mm elbows | m | 14
Carried forward to Next Page
Carried forward from Previous Page
23.7 | 7.12 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 1
23.8 | 7.14 | Flow Test Arrangement
|  | New Flow test arrangement to be installed | PC SUM | 1 |  |  | 50000
23.9 | 7.16 | Gauge Cock Replacement
|  | Replace pressure gauge isolating gauge cock with bleed outlet | No. | 1
23.1 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve 1 & 2 | No. | 40
23.11 | 7.25 | Alarm Motor & Gong Test
|  | Replace alarm motor and gong | No. | 1
23.12 | 7,20 | Drain & Test Pipes
|  | - 25 diam test pipe to drain pt 1m external of chamber | m | 4
|  | - 25 diam elbows | No. | 7
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
|  | - 50 diam elbows | No. | 7
23.13 | 9 - Area 1 Issue 2 | Vertical supports for workshop area:
|  | - 80 mm pipe support | No. | 2
23.13 | 9 - Area 1 Issue 3 | New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 24
|  | - 32 mm diam pipe | m | 24
|  | - 40 mm diam pipe | m | 12
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 6
|  | - 100 mm diam pipe | m | 24
|  | - 25 mm sprinkler equal Tee | No. | 4
|  | - 32 mm sprinkler reducing Tee | No. | 4
|  | - 40 mm sprinkler reducing Tee | No. | 4
|  | - 50 mm sprinkler reducing Tee | No. | 4
|  | - 32 - 25 mm diam reducers | No. | 4
|  | - 40 - 32 mm diam reducers | No. | 4
|  | - 50 - 40 mm diam reducers | No. | 4
|  | - 65 - 50 mm diam reducers | No. | 4
|  | - 80 - 65 mm diam reducers | No. | 4
|  | - 100 - 80 mm diam reducers | No. | 4
|  | - 80 mm diam equal tee | No. | 4
|  | - 100 mm diam equal tee | No. | 4
|  | - Sprinkler Factor K8 | No. | 5
Carried forward to Next Page
Carried forward from Previous Page
23.14 | 9 - Area 1 AE1 Issue 4 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 28
23.15 | 9 - Area 1 Issue 5 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 1
23.16 | 9 - Area 1 AE1 Issue 6 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 1
23.17 | 9 - Area 1 Issue 7 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 97
|  | - Angle iron brackets 100x65x7 mm | m | 242.5
|  | - Perlin clamp | No. | 194
23.18 | 9 - Area 1 Issue 14 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 1
23.19 | 9 - Area 1 Issue 16 | Terminal Range Support
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 20
|  | - Angle iron brackets 100x65x7 mm | m | 60
|  | - Perlin clamp | No. | 40
Carried forward to Next Page
Carried forward from Previous Page
23.2 | 9 - Area 1 Issue 19 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 1
23.21 | 9 - Area 1 Issue 20 | Sprinkler Guards
|  | Sprinkler guards damaged or missing | No. | 1
23.22 | 9 - Area 1 Issue 21 | Sprinkler Alighnment
|  | Sprinkler heads must be correctly aligned | No. | 1
23.23 | 9 - Area 1 Issue 22 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 4
23.24 | 9 - Area 1 Issue 23 | Pipe Supports
|  | No support on the distribution mains | No. | 4
23.25 | 9 - Area 1 Issue 26 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 750 mm from the end of the range pipe
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 97
|  | - Unistrut 41 x 41 mm | m | 242.5
|  | - Unistrut beam clamp | No. | 194
23.26 | 9 - Area 2 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work to canopy and must be rectified. | PC SUM | 1 |  |  | 5000
23.27 | 9 - Area 2 Issue 2 | Sprinklers Installed Beneath Open Cell Surfaces / Translucent Sheeting
|  | Sprinkler shield for 25 mm sprinkler | No. | 96
Carried forward to Next Page
Carried forward from Previous Page
23.28 | 9 - Area 2 Issue 8 | Sprinkler Protection
|  | The sprinklers must be fitted with approved water shields and sprinkler guards so as to prevent mechanical damage | No. | 8
23.29 | 9 - Area 2 Issue 10 | Distribution Pattern of Sprinklers
|  | Remove obstruction | No. | 1
23.3 | 9 - Area 2 Issue 11 | Pipe Supports
|  | Belt-to-belt hangers must be removed and the pipe work correctly supported | No. | 20
Total Carried forward to Summary Page

## 25 Techniplas Frotek
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8483 | FROTEK
Automatic Sprinkler System
24.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
24.2 | 7.11 | Manifold Supported
|  | The valve manifold must be adequately supported. | No. | 1
24.3 | 7.20 | Drain & Test Pipes Installed Correctly
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 4
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
24.4 | 9 - Area 1 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work to canopy and must be rectified. | PC SUM | 1 |  |  | 5000
24.5 | 9 - Area 2 Issue 4 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 3
24.6 | 9 - Area 2 Issue 6 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 3
Carried forward to Next Page
Carried forward from Previous Page
24.7 | 9 - Area 2 Issue 8 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 450 mm from the end of the distribution pipe.
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 1
24.8 | 9 - Area 2 Issue 9 | Range Support
|  | The sprinkler pipe work must be correctly supported. | No. | 8
24.9 | 9 - Area 3 Issue 1 | Partial Protection
|  | - 40 mm diam pipe | m | 3
|  | - 40 mm diam sprinkler reducing tee to 25 mm | No. | 9
|  | - 40 mm diam elbows | No. | 2
|  | - 40 mm sockets | No. | 9
|  | - 80 mm diam pipe | m | 18
Replace corroded pipe:
|  | - 25 mm diam pipe | m | 0
|  | - 32 mm diam pipe | m | 6
|  | - 40 mm diam pipe | m | 6
|  | - 50 mm diam pipe | m | 12
|  | - 65 mm diam pipe | m | 18
|  | - 80 mm diam pipe | m | 18
|  | - 100 mm diam pipe | m | 0
|  | - 150 mm diam pipe | m | 0
|  | - 25 mm sprinkler equal Tee | No. | 3
|  | - 32 mm sprinkler reducing Tee | No. | 3
|  | - 40 mm sprinkler reducing Tee | No. | 3
|  | - 50 mm sprinkler reducing Tee | No. | 0
|  | - 32 - 25 mm diam reducers | No. | 3
|  | - 40 - 32 mm diam reducers | No. | 3
|  | - 50 - 40 mm diam reducers | No. | 3
|  | - 65 - 50 mm diam reducers | No. | 1
|  | - 80 - 65 mm diam reducers | No. | 1
|  | - 100 - 80 mm diam reducers | No. | 0
|  | - 80 mm diam equal tee | No. | 0
|  | - 100 mm diam equal tee | No. | 0
|  | - 80 mm diam elbows | No. | 2
|  | - 100 mm diam ebows | No. | 0
|  | - 65 mm socket | No. | 3
|  | - Sprinkler Factor K8 | No. | 17
Total Carried forward to Summary Page

## 26 FE1 HOP
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8803 | FE1 HOP
Automatic Sprinkler System
25.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
25.2 | 7.20 | Drain & Test Pipes Installed Correctly
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 4
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 4
25.3 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | Sum | 1
25.4 | 9 - Area 1 Issue 1 | Mix of Operating Temperature Sprinklers
|  | The 93 degree Celsius sprinklers under the stairs must be replaced with 68 degree Celsius | No. | 1
25.5 | 9 - Area 2 Issue 2 | Pipe Supports
|  | An additional hangers required. | No. | 30
25.6 | 9 - Area 2 Issue 3 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 3
Carried forward to Next Page
Carried forward from Previous Page
25.7 | 9 - Area 2 Issue 4 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 450 mm from the end of the distribution pipe.
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 40
25.8 | 9 - Area 2 Issue 5 | Heat Collection Plates
|  | Approved heat collection plates to be installed | No. | 10
25.9 | 9 - Area 2 Issue 6 | Pipe Supports
|  | An additional hangers required. | No. | 50
25.1 | 9 - Area 2 Issue 6 | Pipe Supports
|  | Hangers have come adrift and must be re-fixed to their original positions. | No. | 10
25.11 | 9 - Area 3 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work to canopy and must be rectified. | PC SUM | 1 |  |  | 5000
25.12 | 9 - Area 3 Issue 2 | Pipe Supports
|  | Hangers have come adrift and must be re-fixed to their original positions. | No. | 20
Total Carried forward to Summary Page

## 27 Sundale Dairy
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC4761 | Sundale Dairy
Automatic Sprinkler System
26.1 | 7,8 | New Fire Booster Connection
|  | - 100 diam pipe | m | 10
|  | - 100 diam elbow | No. | 6
|  | - 100 diam tee | No. | 2
|  | - 80 mm female couplings | No. | 4
|  | - 100 diam twin booster connection | No. | 2
|  | - 290 mm external signage | No. | 2
|  | Labour to disassemble valves, modify existing feed main. | No. | 2
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 8
26.2 | 7,10 | Flow Switch
Flow switch installed incorrectly, must be down stream from alarm valve with 25 mm test pipe, 2 pipe diameters down stream of flow switch
|  | - 25 mm diam sockets | No. | 2
|  | - 25 mm test pipe | m | 8
|  | - 25 mm elbows | m | 14
26.3 | 7.27 | Chains and Padlocks
- light duty chain
|  | - Padlock barrels to be keyed alike to current EL IDZ master key. | No. | 3
26.4 | 7,2 | Sprinkler Valve Location Plate
|  | A valve location plate must be affixed on an external wall, as near to the main stop valve as possible. | No. | 1
26.5 | 7.12 | Riser Mains Support
|  | The riser main must be properly supported in accordance with the rules | No. | 4
26.6 | 7.25 | Alarm Motor & Gong Test
|  | Replace alarm motor and gong | No. | 2
26.7 | 9 - Area 1 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work to canopy and must be rectified. | PC SUM | 1 |  |  | 5000
Carried forward to Next Page
Carried forward from Previous Page
26.8 | 9 - Area 1 Issue 2 | Partial Protection
|  | Sprinkler protection must be extended in order to provide correct coverage. | No. | 1
26.9 | 9 - Area 1 Issue 3 | Distribution Pattern
|  | Distribution pattern of sprinklers affected. | No. | 3
26.1 | 9 - Area 1 Issue 4 | Painted Sprinklers
|  | Replace sprinklers | No. | 1
26.11 | 9 - Area 1 Issue 6 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 450 mm from the end of the distribution pipe.
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 1
26.12 | 9 - Area 1 Issue 7 | Distribution Pattern
|  | Distribution pattern of sprinklers affected. | PC SUM | 1 |  |  | 5000
26.13 | 9 - Area 1 Issue 8 | Sprinklers Effective Working Distance.
|  | Sprinklers are out of effective working distance. | PC SUM | 1 |  |  | 15000
23.14 | 9 - Area 1 Issue 10 | Sprinklers Effective Working Distance.
|  | Sprinklers are out of effective working distance. | PC SUM | 1 |  |  | 15000
26.15 | 9 - Area 1 Issue 11 | Distribution Pattern
|  | Distribution pattern of sprinklers affected. | PC SUM | 1 |  |  | 5000
26.16 | 9 - Area 1 Issue 12 | Pipe Supports
|  | 1st range hangers are exceeding the maximum distance of 2,0 metres from the distribution pipe. | No. | 1
Carried forward to Next Page
Carried forward from Previous Page
26.17 | 9 - Area 1 Issue 13 | Sprinklers Effective Working Distance.
|  | Sprinklers are out of effective working distance. | PC SUM | 1 |  |  | 5000
26.18 | 9 - Area 1 Issue 14 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 450 mm from the end of the distribution pipe.
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 1
26.19 | 9 - Area 2 Issue 1 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 450 mm from the end of the distribution pipe.
|  | - 32 mm pipe hangar; G clamp and hanging rod | No. | 1
26.2 | 9 - Area 3 Issue 1 | Sprinklers dropped below level of the ceiling
|  | Sprinklers must be re-fixed to their original intended operating position. The hanger supporting it must be checked and, if necessary, re-secured. | No. | 1
26.2 | 9 - Area 4 Issue 1 | The sprinkler heads and piping within the system are over 25 years of age | PC Sum | 1 |  |  | 500000
Total Carried forward to Summary Page

## 28 BW1 BW2 Seraphim
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8476 | BW1 & BW3 Seraphim
Automatic Sprinkler System
28.1 | 4 | Sprinkler System Design
|  | Hydraulic calculations and recommendations to satisfy finding. | Sum | 1
28.2 | 7,7 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New bypass Valve 2 - 100mm Diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
|  | Labour to disassemble & modify existing valves (100 diam . | No. | 1
28.3 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
28.4 | 7.14 | Flow Measuring Device Installed
|  | Installed incorrectly and no requirement on block plan | PC Sum | 1 |  |  | 50000
28.5 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 150 mm diam Valve 1 | No. | 24
|  | Replace bolts to 100 mm diam Valve 2 | No. | 24
28.6 | 7.20 | Drain & Test Pipes Installed Correctly
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 8
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 8
Carried forward to Next Page
Carried forward from Previous Page
28.7 | 7.27 | Pressure
|  | The system pressure has exceeded the maximum allowable pressure of 1200 kPa, this must be investigated and a solution / methodology provided to EL IDZ to correct. | No. | 1
28.9 | 9 - Area 2 Issue 2 | Sprinkler protection required beneath bulkheads which exceed 800mm in depth
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 24
|  | - 32 mm diam pipe | m | 24
|  | - 40 mm diam pipe | m | 12
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 6
|  | - 100 mm diam pipe | m | 24
|  | - 25 mm sprinkler equal Tee | No. | 4
|  | - 32 mm sprinkler reducing Tee | No. | 4
|  | - 40 mm sprinkler reducing Tee | No. | 4
|  | - 50 mm sprinkler reducing Tee | No. | 4
|  | - 32 - 25 mm diam reducers | No. | 4
|  | - 40 - 32 mm diam reducers | No. | 4
|  | - 50 - 40 mm diam reducers | No. | 4
|  | - 65 - 50 mm diam reducers | No. | 4
|  | - 80 - 65 mm diam reducers | No. | 4
|  | - 100 - 80 mm diam reducers | No. | 4
|  | - 80 mm diam equal tee | No. | 4
|  | - 100 mm diam equal tee | No. | 4
|  | - Sprinkler Factor K36 (K Factor Unknown) | No. | 5
28.1 | 9 - Area 2 Issue 4 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 1
28.11 |  | GENERAL NOTE
|  | Must be determined if sprinkler protection can be installed in the laminating machines, this must be investigated and a solution / methodology provided to EL IDZ to correct. | Sum | 1
Total Carried forward to Summary Page

## 29 BW3 Linde & Wiemann
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8477 | BW3 LINDE & WIEMANN
Automatic Sprinkler System
29.1 | 7,5 | Sprinkler Valve Instruction Chart
|  | A weatherproof valve instruction chart that relates specifically to the control valve assembly installed, (not a generic instruction chart) shall be mounted on a wall within the control valve cabinet or if the valves are internally located, as close to these as possible | No. | 1
29.2 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
29.3 | 7.11 | Manifold Supported
|  | The valve manifold must be adequately supported. | No. | 1
29.4 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 150 mm diam Valve 1 | No. | 24
29.5 | 7.25 | Alarm Motor & Gong Test
|  | Replace alarm motor and gong | No. | 1
29.6 | 9 - Area 1 Issue 2 | Sprinkler Alignment
|  | Sprinkler heads must be correctly aligned | No. | 2
Total Carried forward to Summary Page

## 30 AE6
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC10602 | AE6
Automatic Sprinkler System
30.1 | 7.7 | Sprinklers Valves
|  | New Bypass Valve 1 - 150mm diam | No. | 1
- 150 diam pipe
- 150 diam elbows
- 150 diam stop valves (Nibco)
- 150 diam non return valve
- 150 diam Flanged Tees
|  | New bypass Valve 2 - 100mm Diam | No. | 1
- 100 diam pipe
- 100 diam elbows
- 100 diam stop valves (Nibco)
- 100 diam non return valve
- 100 diam Flanged Tee
|  | Labour to disassemble & modify existing valves (100 diam . | No. | 1
30.2 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
30.3 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 150 mm diam Valve 1 | No. | 48
30.4 | 9 - Area 1 Issue 1 | Pipe Supports
|  | Belt-to-belt hangers must be removed and the pipe work correctly supported | No. | 18
Total Carried forward to Summary Page

## 31 D-Fence
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC8801 | D-FENCE
Automatic Sprinkler System
31.1 | 7.8 | Fire Brigade Booster Pressure Connection
|  | Replace 4x existing sockets with 1/2 socket. | No. | 4
31.2 | 7.20 | Drain & Test Pipes Installed Correctly
The drain and test pipes discharge within the valve cabinet. This must be revised so they discharge externally to the valve cabinet.
|  | - 25 diam test pipe to drain pt 1m external of chamber + flow meter. | m | 8
|  | - 50 diam drain pipe to drain pt 1m external of chamber. | m | 8
31.3 | 9 - Area 1 Issue 1 | Corrosion
|  | Corrosion is evident on the sprinkler pipe work to canopy and must be rectified. | PC SUM | 1 |  |  | 5000
31.4 | 9 - Area 1 Issue 2 | Pipe Supports
|  | Distribution rise/drop pipes shall be secured directly to the building structure or by hangers securing horizontal distribution pipes within 300 mm of the riser | No. | 3
Carried forward to Next Page
Carried forward from Previous Page
31.5 | 9 - Area 2 Issue 1 | Corrosion
New range pipe + sprinklers
|  | - 25 mm diam pipe | m | 24
|  | - 32 mm diam pipe | m | 24
|  | - 40 mm diam pipe | m | 12
|  | - 50 mm diam pipe | m | 6
|  | - 65 mm diam pipe | m | 6
|  | - 80 mm diam pipe | m | 6
|  | - 100 mm diam pipe | m | 24
|  | - 25 mm sprinkler equal Tee | No. | 4
|  | - 32 mm sprinkler reducing Tee | No. | 4
|  | - 40 mm sprinkler reducing Tee | No. | 4
|  | - 50 mm sprinkler reducing Tee | No. | 4
|  | - 32 - 25 mm diam reducers | No. | 4
|  | - 40 - 32 mm diam reducers | No. | 4
|  | - 50 - 40 mm diam reducers | No. | 4
|  | - 65 - 50 mm diam reducers | No. | 4
|  | - 80 - 65 mm diam reducers | No. | 4
|  | - 100 - 80 mm diam reducers | No. | 4
|  | - 80 mm diam equal tee | No. | 4
|  | - 100 mm diam equal tee | No. | 4
|  | - Sprinkler Factor K36 | No. | 5
31.6 | 9 - Area 1 Issue 2 | Terminal Range Support
Terminal range pipe hangers are exceeding the maximum distance of 450 mm from the end of the distribution pipe.
|  | - 150 mm pipe hangar; G clamp and hanging rod | No. | 2
Total Carried forward to Summary Page

## 32 ASP Pump House
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
SCHEDULE OF QUANTITIES (PROVISIONAL)
ITEM | FINDING |  | UNIT | QUAN- | SUPPLY | INSTALL | AMOUNT
NO |  |  |  | TITY | RATE | RATE
| UNC9478 | ESTATE PUMP HOUSE
Automatic Sprinkler System
27.1 | ITEM 1 | PC SUM |  |  |  |  | 150000
27.2 | ITEM 2 | PC SUM |  |  |  |  | 150000
27.3 | 6,1,8 | Block Plan
|  | Provide new block plan for Valve 2, with the following information indicated: | No. | 1
- particulars of water supplies
- occupancy of the building
- hazard class of each zone / system
- extent of the protection
- calculated flow and pressure requirements of the system
- cross sectional elevation of the building and or zones, indicated height of highest sprinkler
- flow and pressures for the remote and favourable areas of operation
- maximum pressure
- maximum flow
27.4 | 7.17 | Flange Bolts
Flanges Short Bolted
|  | Replace bolts to 200 mm diam Valve | No. | 12
27.5 | 6,2,11 | Electrical Cables
|  | Electrical cables positioned 300mm above the finished floor level. | PC Sum | 1 |  |  | 50000
Total Carried forward to Summary Page

## Summary
EAST LONDON INDUSTRIAL DEVELOPMENT ZONE
ASIB REMEDIAL WORKS
SPRINKLER INSTALLATIONS TO VARIOUS FACTORIES
PROVISIONAL SCHEDULE OF QUANTITIES
FINAL SUMMARY PAGE
Item No. | Description | Total Amount
1 | SCHEDULE NO 1: PRELIMINARY & GENERAL
2 | ESTATE PUMP HOUSE
3 | AE8
4 | BUSHVELD ENERGY
5 | CE1 LINDE & WIEMANN
6 | BE5 DSV
7 | YEKANI EAST LONDON
8 | GW1 VALEO
9 | GE1 AURIA
10 | HW1 EBOR
11 | HE1 POLYTECH
12 | HS1
13 | CW1 AIC
14 | B2; 4 & 6 LINDE & WIEMANN
15 | BE2 MARTINREA
16 | AW4 MOLAN PINO
17 | AW6 MOLAN PINO
18 | C2 YANFENG
19 | AW8 & 9 YANFENG
20 | AUTOMOILD
21 | ASP TUGGER ROUTE
22 | SOS CHEESE FACTORY
23 | EW1 TIA
24 | FELTEX
25 | TECHNIPLAS
26 | FE1 NOP
27 | SUNDALE
28 | BW1 BW2 Seraphim
29 | BW3 LINDE & WIEMANN
30 | AE6
31 | D-FENCE
32 | ASP PUMP HOUSE
SUBTOTAL (Ex VAT)
VAT @ 15%
TOTAL INCL VAT