## Cover sht
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
ES/24/ELEC/LEACHESBAY/ 40MVA/01
CODE | Site Activities
A | P & G's |  | 0
B | Provisional Sums |  | 4114550
C1 | Civil Works |  | 0
C2 | Steelwork Erection |  | 0
C3 | Equipment Erection |  | 0
C4 | Conductor, Clamps and Earthing |  | 0
C5 | Secondary Plant |  | 0
C6 | Fibre & Power Cabling |  | 0
|  | Sub Total | 4114550
|  | Contingency | 10% | 411455
…………………………………… ………………. |  | 15% Vat | 678900.75
Signature Date |  | Total | 5204905.75

## P & Gs
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
CODE | SANS 1200A |  | STANDARD ACTIVITY | UNIT | QTY | RATE | TENDER PRICE
A.1 | Payment Ref |  | FIXED CHARGE ITEMS
A.1.1 | 8.3.1 |  | Contractual Requirements
|  |  | Contractual requirements i.e., insurance’s, statutory contributions, Guarantees , etc.(For Contract Duration) | sum | 1 |  | 0
A.1.2 | 8.3.2 | .1' | Facilities for the Engineer
|  | (a) | Furnished offices, latrines and carports | sum | 1 |  | 0
|  | (b) | Name boards ( Signboards) | No. | 2 |  | 0
A.1.3 | 8.3.2 | .2' | Facilities for the Contractor
|  | (a) | Offices, fencing and storage sheds | sum | 1 |  | 0
|  | (b) | Workshops | sum | 1 |  | 0
|  | (c) | Laboratories | sum | 1 |  | 0
|  | (d) | Living accommodation | sum | 1 |  | 0
|  | (e) | Ablution and latrine facilities | sum | 1 |  | 0
|  | (f) | Tools and equipment | sum | 1 |  | 0
|  | (g) | Water supplies, power and communication | sum | 1 |  | 0
|  | (h) | Dealing with water (Sub-clause 5.5) | sum | 1 |  | 0
|  | (i) | Access (Sub-clause 5.8) | sum | 1 |  | 0
|  | (j) | Plant | sum | 1 |  | 0
A.1.4 | 8.3.3 |  | Other fixed-charge obligations | sum | 1 |  | 0
A.1.5 | 8.3.4 |  | Removal of Contractor's site establishment on
|  |  | completion | sum | 1 |  | 0
A..1.6 | 8.3.5 |  | Occupational Health and Safety
Compliance with Occupational Health and Safety Act
(Act 85 of 1993) and its regulations and with the
|  |  | Employers Health and Safety Specification | sum | 1 |  | 0
A..1.7 | 8.3.6 |  | Environmental Managemant
|  |  | Compliance with Environmental Management plan | sum | 1 |  | 0
Sub Total | [6 empty] | 0
A.2 | Payment Ref |  | TIME RELATED ITEMS - For Duration of construction ( 12 months)
A.2.1 |  |  | Outages
|  |  | Contractors must allow for outages being done on weekends. | each | 4 |  | 0
|  |  | Provide a detailed breakdown of outage scope complete with time allocation to be handed to the Project Co-ordinator at the outage planning meeting prior to the outage - [minimum of 48 hours] | each | 4 |  | 0
A.2.2 |  |  | Programme and Planning
|  |  | Contractors must allow for the preparation of a detailed programme reflecting the outage dates. | each | 4 |  | 0
A.2.3 | 8.4.1 |  | Contractual requirements
|  |  | Operation and maintenance of facilities on the Site for | sum | 1 |  | 0
the duration of construction
A.2.4 | 8.4.2 | .1' | Facilities for the Engineer
|  |  | Furnished offices, latrines and carports | sum | 1 |  | 0
A.2.6 | 8.4.2 | .2' | Facilities for the Contractor
|  | (a) | Offices and storage sheds | sum | 1 |  | 0
|  | (b) | Workshops | sum | 1 |  | 0
|  | (c) | Laboratories | sum | 1 |  | 0
|  | (d) | Living accommodation | sum | 1 |  | 0
|  | (e) | Ablution and latrine facilities | sum | 1 |  | 0
|  | (f) | Tools and equipment | sum | 1 |  | 0
|  | (g) | Water supplies, power and communication | sum | 1 |  | 0
|  | (h) | Dealing with water (Sub-clause 5.5) | sum | 1 |  | 0
|  | (i) | Access (Sub-clause 5.8) | sum | 1 |  | 0
|  | (j) | Plant | sum | 1 |  | 0
A.2.7 | 8.4.3 |  | Supervision for duration of construction | sum | 1 |  | 0
A.2.8 | 8.4.4 |  | Company and head office overhead costs for the duration
|  |  | of the contract | sum | 1 |  | 0
A.2.9 | 8.4.5 |  | Other time-related obligations | sum | 1 |  | 0
A.2.10 |  |  | Site security
|  |  | Provide security for entire site untill handover ( 24HR/day) | months | 13 |  | 0
A.2.11 | 8.4.6 |  | Occupational Health and Safety
Compliance with Occupational Health and Safety Act
(Act 85 of 1993) and its regulations and with the
|  |  | Employers Health and Safety Specification | sum | 1 |  | 0
A.2.12 | 8.4.7 |  | Environmental Managemant
|  |  | Compliance with Environmental Management plan | sum | 1 |  | 0
Sub Total | [6 empty] | 0
Total 'A' | [6 empty] | 0

## Prov Sums
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
CODE | SANS 1200A |  | STANDARD ACTIVITY | UNIT | QTY | RATE | TENDER PRICE
B | Payment Ref |  | PROVISIONAL SUMS
SUMS STATED PROVISIONALLY BY THE ENGINEER
For work to be executed by the Contractor and valued
in terms of the "Valuation of Variations" clause in the
Conditions of Contract
ALLOWANCES
| 8.5 |  | Community Requirements
B.1 |  | .1 | CLO/LDO remuneration | Prov Sum | 1 | 110500 | 110500
|  | .2 | Overheads, charges and profit on above | % | 10 | 11050 | 11050
B.2 |  | .1 | Accredited and approved training courses for selected personnel, local and other labourers | Prov Sum | 1 | 80000 | 80000
|  | .2 | Overheads, charges and profit on above | % | 10 | 8000 | 8000
B.3 |  | .1 | Grading of access road/Specialised rigging | Prov Sum | 1 | 600000 | 600000
|  | .2 | Overheads, charges and profit on above | % | 10 | 60000 | 60000
B.3 |  | .1 | Thermal Scanning | Prov Sum | 1 | 50000 | 50000
|  | .2 | Overheads, charges and profit on above | % | 10 | 5000 | 5000
| 8.5 |  | SPECIALIST SERVICES
0
B.4 |  | .1 | Payment of land surveyor | Prov Sum | 1 | 75000 | 75000
|  | .2 | Overheads, charges and profit on above | % | 10 | 7500 | 7500
0
B.5 |  | .1 | Payment of Enviromentalist and OHS Agent ( Eskom Approved) | Prov Sum | 1 | 585000 | 585000
|  | .2 | Overheads, charges and profit on above | % | 10 | 58500 | 58500
B.6 |  | .1 | Cross-cut to expose existing services | Prov Sum | 1 | 50000 | 50000
|  | .2 | Overheads, charges and profit on above | % | 10 | 5000 | 5000
B.7 |  | .1 | Relocating existing services | Prov Sum | 1 | 50000 | 50000
|  | .2 | Overheads, charges and profit on above | % | 10 | 5000 | 5000
B.8 |  | .1 | Facilitation of all Wayleave extensions | Prov Sum | 1 | 40000 | 40000
|  | .2 | Overheads, charges and profit on above | % | 10 | 4000 | 4000
B.9 |  | .1 | Construction Supervision by Clerk of Works (Under Engineer) | Prov Sum | 1 | 950000 | 950000
|  | .2 | Overheads, charges and profit on above | % | 10 | 95000 | 95000
B.10 |  | .1 | Installation and Commissioning of Transformer 5JB-3200 & 5TM3100 Schemes by OEM | Prov Sum | 1 | 850000 | 850000
|  | .2 | Overheads, charges and profit on above | % | 10 | 85000 | 85000
B.11 |  | .1 | Engineers Subsistence allowance | Prov Sum | 1 | 300000 | 300000
|  | .2 | Overheads, charges and profit on above | % | 10 | 30000 | 30000
Total 'B' | [6 empty] | 4114550

## Civil Work 1
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C1 |  | Civil Works
1.1 |  | Extra over all excavations:
1.1.1 |  | Intermediate material (Provisional amount). | m³ | 100 |  |  | 0
1.2 |  | Extra over all excavations:
1.2.1 |  | Hard rock material (Provisional amount). | m³ | 100 |  |  | 0
1.3 |  | Bench marker:
1.3.1 |  | Supply and install and maintain: | no | 1 |  |  | 0
1.4 |  | Paving bricks:
1.4.1 |  | Supply, prepare surface area and install. | m² | 0 |  |  | 0
1.5 |  | Stone kerbing:
1.5.1 |  | Supply, prepare area and install. | m | 0 |  |  | 0
1.6 |  | Road stone (9mm):
1.6.1 |  | Supply, prepare area and install. | m² | 3 |  |  | 0
1.7 | D-DT-6366-1 | Yard stone (26/38mm):
1.7.1 |  | Supply, prepare surface area and install. | m³ | 244 |  |  | 0
1.8 |  | Cable trench kerbing:
1.8.1 |  | Supply, prepare area and install. | m | 186 |  |  | 0
1.9 | D-EC-1735-1/2 | Cable trench cover (750mm):
1.9.1 |  | Supply and install. | m | 90 |  |  | 0
1.10 |  | Cable trench cover (1500mm):
1.10.1 |  | Supply and install. | m | 0 |  |  | 0
1.11 |  | Road crossing cable trench (10 Pipe):
1.11.1 |  | Supply, prepare and install 10 pipe cable trench, entrance, wing walls & covers (11m). | no | 1 |  |  | 0
1.12 |  | Palisade gate ramp (1m):
1.12.1 |  | Supply and install . | no | 0 |  |  | 0
1.13 |  | Palisade gate ramp (2.5m):
1.13.1 |  | Supply and install . | no | 0 |  |  | 0
1.14 |  | Palisade gate ramp (5m):
1.14.1 |  | Supply and install . | no | 0 |  |  | 0
1.15 |  | Column foundations (132kV):
1.15.1 |  | Supply and install. | no | 0 |  |  | 0
1.16 | D-DT-5220-1A | Tubular busbar foundation (132kV):
1.16.1 |  | Supply and install (TB11 - TB14). | no | 4 |  |  | 0
1.17 | D-DT-5200-1A | Breaker foundation (132kV):
1.17.1 |  | Supply and install (CB6). | no | 1 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Civil Work 2
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C1 |  | Civil Works (Continued) Balance B/F |  |  |  |  | 0
1.18 | D-DT-5202-1A | Isolator foundation (132kV):
1.18.1 |  | Supply and install (IS15-IS16). | no | 2 |  |  | 0
1.19 | D-DT-5206-1A | Medium equipment support foundations:
1.19.1 |  | Supply and install (CT19 - CT21, PI25 - PI28). | no | 7 |  |  | 0
1.20 | D-DT-5217-1B | Lighting mast foundations (14m):
1.20.1 |  | Supply, prepare area and install (LM7-LM11). | no | 5 |  |  | 0
1.21 | D-EC-1973-9B | Two Winding Transformer Plinth , Slipway , Drainage & Oil Catchment Area Connected To Oil Dam - Front Entry 40MVA:
1.21.1 |  | Supply, prepare area and install (T3). | no | 1 |  |  | 0
1.22 | D-DT-5207-1A | NECR'T/ AUX.TRFR Foundation (11kV)
1.22.1 |  | Supply and install (NEC3). | no | 1 |  |  | 0
1.23 | D-EC-1974-1 | Road Crossing Foundation
1.23.1 |  | Supply and install (RC5-RC6). | no | 2 |  |  | 0
1.24 | D-DT-5205-1A | Isolator foundation (22kV):
1.24.1 |  | Supply and install (IS17). | no | 1 |  |  | 0
1.25 | D-DT-5213-1A | MV Cable Sealing End Fundation
1.25.1 |  | Supply and install (CSE3). | no | 1 |  |  | 0
1.26 | D-DT-5416-22 | Transformer PIU Foundation and concrete Plinth 600mm x 1000mm:
1.26.1 |  | Supply, prepare area and install. | no | 1 |  |  | 0
1.27 | D-DT-5234-1A | Oil Holding Dam
1.27.1 |  | Supply and install (D1). | no | 1 |  |  | 0
1.28 |  | Drainage Concrete Pipes (300mm)
1.28.1 |  | Supply and install | m | 100 |  |  | 0
1.29 |  | Weed killer:
1.29.1 |  | Supply and spray. | m2 | 6040 |  |  | 0
1.30 |  | Waste bins:
1.30.1 |  | Supply bins for waste materials. | no | 4 |  |  | 0
1.31 |  | Waste bins disposal:
1.31.1 |  | Removable of waste material from site to nearest municipal tip. | trips | 16 |  |  | 0
1.32 |  | Excess material:
1.32.1 |  | Remove excess material from platform and dispose of within site boundary and level. | m³ | 120 |  |  | 0
1.33 |  | Interface Junction Box (132kV):
1.33.1 |  | Supply and install (JB1). | no | 0 |  |  | 0
1.34 |  | Provision:
1.34.1 |  | Demolishing of the existing oil dam (5mx3mx1,5m) and the removal of the ruble from the site | Sum | 1 |  |  | 0
|  | Total C1 |  |  |  |  | 0

## Steel Erection 1
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C2 |  | Erection of Steelwork
2.1 |  | Palisade fence:
2.1.1 |  | Supply, prepare area and install. | m | 0 |  |  | 0
2.2 |  | Palisade fence (Modified):
2.2.1 |  | Supply, prepare area and install (Modified panels 0 - 3m). | no | 0 |  |  | 0
2.3 |  | Palisade fence gate (1m):
2.3.1 |  | Supply and install palisade gate. | no | 0 |  |  | 0
2.4 |  | Palisade fence gate (2.5m):
2.4.1 |  | Supply and install palisade gate. | no | 0 |  |  | 0
2.5 |  | Palisade fence gate (5m):
2.5.1 |  | Supply and install palisade gate. | no | 0 |  |  | 0
2.6 |  | Palisade fence brackets and labels:
2.6.1 |  | Supply and install label brackets and labels. | item | 0 |  |  | 0
2.7 |  | Columns 132kV (MK132/C type):
2.7.1 |  | Supply, assemble, erect and bolt in position. | no | 0 |  |  | 0
2.8 |  | Earth wire supports (132kV):
2.8.1 |  | Supply, assemble, erect and bolt in position. | no | 0 |  |  | 0
2.9 |  | Beam 132kV (Type 132/40/1):
2.9.1 |  | Supply, assemble, erect and bolt in position. | no | 0 |  |  | 0
2.10 |  | "U" bolts:
2.10.1 |  | Supply and install. | no | 20 |  |  | 0
2.11 | D-DT-5220-2 | Tubular busbar support (132kV):
2.11.1 |  | Supply, assemble, erect and bolt in position (TB11 - TB14). | no | 4 |  |  | 0
2.12 | D-DT-5200-2A | Breaker support (132kV):
2.12.1 |  | Supply, erect and bolt in position (CB6). | no | 1 |  |  | 0
2.13 | D-DT-5202-2A | Isolator standard support (132kV):
2.13.1 |  | Supply, assemble, erect and bolt in position (IS15). | no | 1 |  |  | 0
2.14 | D-DT-5202-2I | Isolator inline support (132kV):
2.14.1 |  | Supply, assemble, erect and bolt in position (IS16). | no | 1 |  |  | 0
2.15 | D-DT-5206-2C | Medium equipment support (2,5m):
2.15.1 |  | Supply, assemble, erect and bolt in position (CT19 - CT21 & PI25 - PI28). | no | 7 |  |  | 0
2.16 | D-DT-5206-2H | Medium equipment cap detail (M1):
2.16.1 |  | Supply, assemble, erect and bolt in position (CT19 - CT21 & PI25 - PI28). | no | 7 |  |  | 0
2.17 | D-DT-5217-2B | Lightning mast (14m):
2.17.1 |  | Supply, assemble, erect and bolt in position (LM7-LM11). | no | 5 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Steel Erection 2
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C2 |  | Erection of Steelwork (Continued) Balance B/F |  |  |  |  | 0
2.18 | D-EC-1974-2 | Road crossing support:
2.18.1 |  | Supply, assemble, erect and bolt in position (RC5-RC6). | no | 2 |  |  | 0
2.19 | D-DT-5207-2A | NECR'T/AUX.TRFR support (11kV):
2.19.1 |  | Supply, assemble, erect and bolt in position (NEC3). | no | 1 |  |  | 0
2.20 | D-DT-5205-2A | Isolator support (22kV):
2.20.1 |  | Supply, assemble, erect and bolt in position (IS17). | no | 1 |  |  | 0
2.21 | D-DT-5219-1 | Surge arrestor bracket (11kV):
2.21.1 |  | Supply, assemble, erect and bolt in position (SA9). | no | 1 |  |  | 0
2.22 | D-DT-5213-2D | MV Cable End Support (11kV)
2.22.1 |  | Supply, assemble, erect and bolt in position (CSE3). | no | 1 |  |  | 0
2.23 | D-DT-5416-2 | 5JB-3200 Transformer PIU Stainless Steel Junction box
2.23.1 |  | Supply, assemble, erect and bolt in position (PIU). | no | 1 |  |  | 0
2.24 |  | Cable support bracket (medium equipment support 2,5m) :
2.24.1 |  | Supply and bolt in positions (CT19- CT21). | no | 3 |  |  | 0
2.25 |  | JB brackets ( 132kV Busbar isolators):
2.25.1 |  | Supply and bolt in positions (JB15 - JB16). | no | 2 |  |  | 0
2.26 | D-DT-6114-2 | Bracket (Phasing discs label):
2.26.1 |  | Supply and bolt in position (D31 - D42). | no | 12 |  |  | 0
2.27 |  | Bracket (Busbar label):
2.27.1 |  | Supply and bolt in position (LB11 - LB14). | no | 4 |  |  | 0
2.28 |  | M12 x 45mm Gal. Steel set screw bolts, washers & tapper washers for SA's.
2.28.1 |  | Supply and install (SA31- SA33). | no | 12 |  |  | 0
2.29 |  | M12 x 65mm Stainless steel set screw bolts & 2 x washers/bolt for breaker palm clamps:
2.29.1 |  | Supply and install (CB6). | no | 24 |  |  | 0
2.30 |  | M12 x 65mm Stainless steel set screw bolts & 2 x washers/bolt for isolators palm clamps:
2.30.1 |  | Supply and install (IS15 - IS16, IS17). | no | 72 |  |  | 0
2.31 |  | M16 x 35mm Gal. Steel set screw bolts, washers & tapper washers for post Insulators.
2.23.1 |  | Supply and install (PI25 - PI28, TB11 - TB14 & RC5-RC6). | no | 80 |  |  | 0
2.32 |  | M16 x 30mm Gal. Steel set screw bolts & washers for post Insulators clamps.
2.32.1 |  | Supply and install (PI25 - PI28, TB11 - TB14 & RC5-RC6). | no | 80 |  |  | 0
2.33 |  | M16 x 40mm Gal. steel bolts, washers & tapper washers for equipment.
2.33.1 |  | Supply and install (CT19- CT21 & SA31-SA33). | no | 24 |  |  | 0
2.34 |  | Control cable bracket
2.34.1 |  | Supply and install. | no | 64 |  |  | 0
|  | Total C2 |  |  |  |  | 0

## Equipment Erection 1
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C3 |  | Erection of Equipment
3.1 | D-DT-6250-1 | Breaker three pole (132kV):
3.1.1 |  | Take delivery, assist with erection and bolt in position (CB6). | no | 1 |  |  | 0
3.2 | D-DT-6190-1 | Current transformers (132kV):
3.2.1 |  | Take delivery, erect and bolt in position (CT19 - CT21). | no | 3 |  |  | 0
3.3 | D-DT-6302-1 | Isolator standard (132kV):
3.3.1 |  | Take delivery, erect and bolt in position (IS15). | no | 1 |  |  | 0
3.4 | D-DT-6302-4 | Isolators inline (132kV):
3.4.1 |  | Take delivery, erect and bolt in position (IS16). | no | 1 |  |  | 0
3.5 | D-DT-6210-1 | Surge station class surge arrestor (132kV):
3.5.1 |  | Take delivery, erect and bolt in position (SA25 - SA27). | no | 3 |  |  | 0
3.6 | D-DT-6230-1 | Post insulators (132kV):
3.6.1 |  | Take delivery, erect and bolt in position (PI25 - PI28, TB11 - TB14 & RC5-RC6 ). | no | 10 |  |  | 0
3.7 | D-DT-6009-1 | Flood lights:
3.7.1 |  | Supply and install (LM1 - LM11). | no | 44 |  |  | 0
3.8 | D-DT-6120-2 | Two winding Transformer (132/11kV 40MVA)
3.8.1 |  | Take delivery, assist with erection and bolt in position (T3). | no | 1 |  |  | 0
3.9 | D-DT-6216-1 | Surge arrestors (11kV):
3.9.1 |  | Take delivery, erect and bolt in position (SA28 - SA33). | no | 6 |  |  | 0
3.10 | D-DT-6140-1 | NEC/NER/AUX TFR (11kV)
3.10.1 |  | Take delivery, erect and bolt in position (NEC3). | no | 1 |  |  | 0
3.11 | D-DT-6305-1 | Isolator (22kV):
3.11.1 |  | Take delivery, erect and bolt in position (IS17). | no | 1 |  |  | 0
3.12 | D-DT-6232-1 | Post insulators (66kV):
3.12.1 |  | Take delivery, erect and bolt in position (CSE3 ). | no | 6 |  |  | 0
3.13 | D-DT-6114-1 | Label (Phasing discs Red):
3.13.1 |  | Supply and bolt in position Red (D31, D36, D37, D40). | no | 4 |  |  | 0
3.14 | D-DT-6114-1 | Label (Phasing discs White):
3.14.1 |  | Supply and bolt in position White (D32, D35, D38, D41). | no | 4 |  |  | 0
3.15 | D-DT-6114-1 | Label (Phasing discs Blue):
3.15.1 |  | Supply and bolt in position Blue (D33, D34, D39, D42). | no | 4 |  |  | 0
3.16 | D-DT-5047 | Labels (Equipment):
3.16.1 |  | Supply and install as per label schedule. | no | 13 |  |  | 0
3.17 |  | Locks and key tags (Equipment):
3.17.1 |  | Supply and install as per label schedule. | no | 20 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Equipment Erection 2
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C3 |  | Erection of Equipment (Continued) Balance B/F |  |  |  |  | 0
3.18 |  | Shark netting (50m rolls):
3.18.1 |  | Supply. | no | 1 |  |  | 0
3.19 |  | Substation earths:
3.19.1 |  | Supply (6m sets). | no | 3 |  |  | 0
3.20 |  | Substation earths:
3.20.1 |  | Supply (4m sets). | no | 6 |  |  | 0
3.21 |  | Substation link stick:
3.21.1 |  | Supply 132kV telescopic link stick. | no | 1 |  |  | 0
3.22 |  | Substation mimic board:
3.22.1 |  | Supply and install "A1". | no | 0 |  |  | 0
3.23 |  | Substation key panel:
3.23.1 |  | Supply and install. | no | 1 |  |  | 0
3.24 |  | Fire extinguishers:
3.24.1 |  | Supply and install fire extinguishers with class fiber box: | no | 0 |  |  | 0
3.25 |  | Fire extinguishers:
3.25.1 |  | Supply and install fire extinguishers with wall bracket: | no | 0 |  |  | 0
3.26 |  | Office desk and chair:
3.26.1 |  | Supply desk and chair. | no | 0 |  |  | 0
3.27 |  | Transport:
3.27.1 |  | Transport secondary / primary plant equipment with LDV 1 ton vehicle: | km | 2000 |  |  | 0
3.28 |  | Transport:
3.28.1 |  | Transport secondary / primary plant equipment with LDV 8 ton vehicle: | km | 2000 |  |  | 0
3.29 |  | All ancillaries and accessories to ensure function operation.
3.29.1 |  | Supply or install | sum | 1 |  |  | 0
3.30 |  | JB (Plug Box PI25 - PI28):
3.30.1 |  | Take delivery and bolt in positions (Plug box). | no | 4 |  |  | 0
3.31 |  | JB (132kV Busbar isolators IS15 & IS6 ):
3.31.1 |  | Take delivery and bolt in positions (JB15 - JB16). | no | 2 |  |  | 0
3.32 |  | JB (132kV CT19 - CT21):
3.32.1 |  | Take delivery and bolt in positions (JB19 - JB21). | no | 1 |  |  | 0
3.33 |  | JB (Interface junction box):
3.33.1 |  | Take delivery and bolt in positions (JB1). | no | 0 |  |  | 0
3.34 |  | Primary plant equipment
3.34.1 |  | Testing and pre-commissioning. | sum | 1 |  |  | 0
3.35 |  | Allow for final Hand-Over Certificate documentation:
3.35.1 |  | Final hand-over | sum | 1 |  |  | 0
3.36 |  | FAT and SAT Testing of Primary Plant Equipment
3.36.1 |  | FAT and SAT Testing | sum | 1 |  |  | 0
|  | Total C3 |  |  |  |  | 0

## Decommissioning (1) (hidden)
#REF!
Item No. | Ref. DRG. No. Proj. Specification | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total | Total | Total Price
[7 empty] | Material Cost | Labour Cost | Rands
C7 |  | Decommissioning
7.1
7.1.1
7.2
7.2.1
7.3
7.3.1
7.4
7.4.1
7.5
7.5.1
7.6
7.6.1
7.7
7.7.1
7.8
7.8.1
7.9
7.9.1
7.10
7.10.1
7.11
7.11.1
7.12
7.12.1
7.13
7.13.1
7.14
7.14.1
7.15
7.15.1
7.16
7.16.1
7.17
7.17.1
Total C7

## Free issue (hidden)
#REF!
Free issue material
QTY | kV | Equipment | Description | mm/kV | Stem dia mm | Sap No.
3 | 66 | Isolator | 1600A 25kA | 31 | 38 | 0012945
6 | 66 | Current transformers | 2P class X 2M class 0.2 | 31 | 38 | 0180035
2 | 66 | Breakers 3P | 1600A 20kA | 31 | 8 hole pad | 0170220
2 | 66/11 | TRFR | 20MVA | 31 | 26 | 0185763
2 | 22 | NEC/NER/AUX Trfr & supp. | 360A 100kVa | 31 | 26 | 0182732
6 | 22 | Breakers & Supports | 1250A 20kA | 31 | 38 | 0170218
16 | 22 | Isolator | 2500A 25kA | 31 | 38 | 0012904
9 | 66 | Surge Arrestor | 10kA | 31 | 26 | 0004562
18 | 11 | Surge Arrestor | 10kA | 31 | M12 lug | 0004626
6 | 11 | Voltage transformers | 100VA class 0.2m+100VA | 31 | 26 | 0008751
3 | 66 | Voltage transformers | 10kA | 31 | 26 | 0180091
24 | 66 | Post Insulator | - | 31 | - | 0017527
- | - | - | - | - | - | -
- | - | - | - | - | - | -
- | - | - | - | - | - | -
QTY | Type | Description |  | Size in mm |  | Sap No.
6 | K-1 | Clamps (Bolted-Bolted) for Stranded Conductors |  | 16,3 to 26 | - | 0005684
15 | K-2 | Clamps (Bolted-Bolted) for Stranded Conductors |  | 26,5 to 26 | - | 0005626
24 | K-3 | Clamps (Bolted-Bolted) for Stranded Conductors |  | 16,3 to 38 | - | 0005685
6 | K-4 | Clamps (Bolted-Bolted) for Stranded Conductors |  | 26,5 to 38 | - | 0005634
6 | K-5 | Clamps (Bolted-Bolted) for Stranded Conductors |  | 38,3 to 38 | - | 0005151
30 | TC-3 | Clamps (Bolted-Compression) for Stranded Conductors |  | 26,5 to 26,5 | - | 0005650
6 | TC-9 | Clamps (Bolted-Compression) for Stranded Conductors |  | 38,3 to 26,5 | - | 0005659
102 | TC-10 | Clamps (Bolted-Compression) for Stranded Conductors |  | 38,3 to 38,3 | - | 0005651
3 | UT-3 | Tee Clamps (Bolted-Compression) for Stranded Conductors |  | 12- 9 to 22-29 | - | 0005638
9 | KC-1 | Stud Clamps (Bolted-Compression) for Stranded Conductors |  | 26 to 26,5 | - | 0005649
24 | KC-2 | Stud Clamps (Bolted-Compression) for Stranded Conductors |  | 38 to 26,5 | - | 0005658
132 | KC-3 | Stud Clamps (Bolted-Compression) for Stranded Conductors |  | 38 to 38,3 | - | 0005660
12 | SPC-1 | Palm Clamps (Bolted-Compression) for Stranded Conductors |  | 26,5 to (50x50) | - | 0005159
12 | ACC-3 | Acrylic clamp cover |  | 26,5 to (50x50) | - | 0011496
6 | EPC-38 | Clamp peg |  | - | - | 0005176
6 | TBEC-120/P | Tubular bus End cap (plain) |  | - | - | 0206319
18 | TBTO-120 | Tubular bus palm tap-off clamp |  | - | - | -
12 | TBFS-120/127 | Fixed bus support clamp |  | - | - | 0213925
12 | TBSC-120/127 | Slider type fixed bus support clamp |  | - | - | 0206341
12 | TBSI-120/38 | Bus stud Terminal Clamp (In-Line) |  | - | - | 0206323
33 | - | 66kV Longrod Insulators 31mm/kV |  | - | - | 0167609
60 | - | 22kV Longrod Insulators 31mm/kV |  | - | - | 0167574
24 | - | Clamp Pistol 4B 30mm – 40mm D6042 |  | - | - | 0011073
30 | - | Clamp Pistol 4B 19mm – 28,6mm D6046 |  | - | - | 0011074
16 | - | Clamp Pistol 4B 5mm – 16mm D7022 |  | - | - | 0185253
572 | - | Meters Centipede Conductor 37/3 78mm AL |  | - | - | 0014447
594 | - | Metres Bull Conductor 61/4 26mm AL |  | - | - | 0014452
456 | - | Metres Bull PVC insulated Conductor 61/4. 26mmAL |  | - | - | 0014761
48 | - | Metres Hornet PVC insulated Conductor 19/3.25mmAL |  | - | - | 0014759
150 | - | Meters Hare Conductor 6/4.72mmAL 1/4.72mm ST |  | - | - | 0014441
| - | kg Flat Copper Bar |  | - | - | 0017204
60 | - | Ball joint, single earth assembly |  | - | - | 0168718
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -
- | - | - |  | - | - | -

## Cond-clamps-earthing 1
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C4 |  | Conductor, Clamps and Earthing
4.1 | D-DT 3136-7 | Jumpers, Bull conductor (0 - 10m):
4.1.1 |  | Take delivery, prepare and install (UNGRS) | no | 7 |  |  | 0
4.2 | D-DT 3136-8 | Jumpers, Bull conductor (0 - 10m):
4.2.1 |  | Take delivery, prepare and install (INSU UNGRS). | no | 7 |  |  | 0
4.3 | D-DT 3136-8 | Jumpers, Centipede conductor (0 - 10m):
4.3.1 |  | Take delivery, prepare and install (INSU UNGRS). | no | 2 |  |  | 0
4.4 | D-DT 3136-8 | Jumpers, Hornet conductor (0 - 10m):
4.4.1 |  | Take delivery, prepare and install (INSU UNGRS). | no | 2 |  |  | 0
4.5 | D-DT-6000-1 | Aluminium tubes (TUBE:BUSBAR;LG 12 M;OD 120 MM;ID 112 MM):
4.5.1 |  | Take delivery, cut to size and install. | no | 10 |  |  | 0
4.6 | D-DT-3074-2 | LUG,AL HORNET 1B M12 0 DEG I/C
4.6.1 |  | Take delivery, prepare and install | no | 7 |  |  | 0
4.7 | D-DT-6109-2 | CLAMP:EYC-T;COMP/PALM 90DG;2X38.3 MM
4.7.1 |  | Take delivery, prepare and install | no | 7 |  |  | 0
4.8 | D-DT-6002-2 | CLAMP:EX-C;BOLT/BOLT; STEM 38 COND 16.3
4.8.1 |  | Take delivery, prepare and install | no | 7 |  |  | 0
4.9 | D-DT-6115-1 | CLAMP, PEG AL BULL 38.3mm EPC-38
4.9.1 |  | Take delivery, prepare and install | no | 18 |  |  | 0
4.10 | D-DT-6002-2 | CLAMP:EX-D;BOLT/BOLT; STEM 38 COND 26.5
4.10.1 |  | Take delivery, prepare and install | no | 7 |  |  | 0
4.11 | D-DT-6002-2 | CLAMP:EX-B;BOLT/BOLT; STEM 26 COND 26.5
4.11.1 |  | Take delivery, prepare and install | no | 4 |  |  | 0
4.12 | D-DT-6013-2 | CLAMP:EYC-B;2X38.3 COMP 38 BOLTED 0DG
4.12.1 |  | Take delivery, prepare and install | no | 4 |  |  | 0
4.13 | D-DT-6006-2 | CLAMP:EXC-C;BOLT/COMP; STEM 38 COND38.3
4.13.1 |  | Take delivery, prepare and install | no | 10 |  |  | 0
4.14 | D-DT-6002-2 | CLAMP:EX-E;BOLT/BOLT; STEM 38 COND 38.3
4.14.1 |  | Take delivery, prepare and install | no | 6 |  |  | 0
4.15 | D-DT-6018-3 | CLAMP:EPC-D;COMP/PALM ODG;38.3 MM
4.15.1 |  | Take delivery, prepare and install | no | 13 |  |  | 0
4.16 | D-DT-6018-3 | CLAMP:EPC-E;COMP/PALM 45DG;38.3 MM
4.16.1 |  | Take delivery, prepare and install | no | 4 |  |  | 0
4.17 | D-DT-6018-3 | CLAMP:EPC-F; COMP/PALM 90DG;38.3MM
4.17.1 |  | Take delivery, prepare and install | no | 3 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Cond-clamps-earthing 2
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C4 |  | Conductor, Clamps and Earthing (Continued) Balance B/F |  |  |  |  | 0
4.18 | D-DT-6029-2 | CLAMP:EXCP-D;PI MOUNT;38.3 MM;PCD 127
4.18.1 |  | Take delivery, prepare and install | no | 5 |  |  | 0
4.19 | D-DT-6081-1 | JOINT, BALL PORTABLE EARTH 20kA G/S
4.19.1 |  | Take delivery, prepare and install | no | 39 |  |  | 0
4.20 | D-DT-6090-6 | CLAMP,TUBE:ETP-TE-IL2-R;120/2X38.3;0D
4.20.1 |  | Take delivery, prepare and install | no | 10 |  |  | 0
4.21 | D-DT-6040-5 | CLAMP,TUBE:ETEC-DC-C;120/4;38.3C-ENDCAP
4.21.1 |  | Take delivery, prepare and install | no | 4 |  |  | 0
4.22 | D-DT-6040-2 | CLAMP,TUBE:ETEC-PL-C;120/4;PLAIN- ENDCAP
4.22.1 |  | Take delivery, prepare and install. | no | 7 |  |  | 0
4.23 | D-DT-6039-2 | CLAMP,TUBE:ESC-PI-F-F;120/127;FIXED
4.23.1 |  | Supply, prepare and install. | no | 7 |  |  | 0
4.24 | D-DT-6316-2 | CLAMP,TUBE:ESC-PI-S-F;120/127;SLIDE
4.24.1 |  | Supply, prepare and install: | no | 7 |  |  | 0
4.25 | D-DT-6117-1 | CLAMP,TUB BUS/PALM T/OFF TBPT120
4.25.1 |  | Supply, prepare and install: | no | 5 |  |  | 0
4.25 |  | Flexible earth leads (Current transformers):
4.25.1 |  | Supply, prepare and install. | no | 10 |  |  | 0
4.26 |  | Flexible earth leads (JB's):
4.26.1 |  | Supply, prepare and install. | no | 9 |  |  | 0
4.27 |  | Main Earth mat , round 10mm:
4.27.1 |  | Trenching | m³ | 50 |  |  | 0
4.27.2 |  | Install Horizontal Grid (10mm annealed round copper - 0.7kg/m) | m | 100 |  |  | 0
4.28 |  | Equipment Earth Tails (50x3mm - 1.38kg/m) :
4.28.1 |  | Supply, prepare and install. | m | 280 |  |  | 0
4.29 |  | Outdoor equipment steel structure earthing:
4.29.1 |  | Supply, prepare and install. | no | 70 |  |  | 0
4.30 |  | Vertical 16mm rods:
4.30.1 |  | Supply, prepare and install. | m | 100 |  |  | 0
4.31 |  | Exo-welding (bonding):
4.31.1 |  | Supply, prepare and bond. | no | 40 |  |  | 0
4.32 |  | Backfill and compaction:
4.32.1 |  | Prepare , backfill and compact. | m³ | 50 |  |  | 0
4.33 |  | Yard stones (100mm thickness):
4.33.1 |  | Supply, prepare and install. | m2 | 100 |  |  | 0
4.34 |  | Shark netting (50m rolls):
4.34.1 |  | Supply, prepare and install. | no | 1 |  |  | 0
4.35 |  | Indoor equipment earthing for 11 kV Switchgear panels & Control panles
4.35.1 |  | Supply, prepare and install. | no | 14 |  |  | 0
4.36 |  | Portable Earth
4.36.1 |  | Complete portable earthing set including link sticks and flexible connectors to suit tubular aluminium busbars with an outer diameter of 120 mm (complete set) | no | 4 |  |  | 0
4.36.2 |  | Complete portable earthing set, including link sticks and flexible connectors to suit stranded aluminium conductor with a diameter of 23,4mm - 38mm. (Complete set) | no | 4 |  |  | 0
4.37 |  | Measure Earthgrid Resistance
4.37.1 |  | Soil resistivity testing and report | no | 1 |  |  | 0
4.38 |  | Fence and gate bonding
4.38.1 |  | Supply, prepare and bond. | no | 2 |  |  | 0
4.39 |  | Provision
4.39.1 |  | Reinstating the main earth bar | Sum | 1 |  |  | 0
|  | Total C4 |  |  |  |  | 0

## Secondary Plant 1
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C5 |  | Secondary Plant
5.1 | D-DT-3128 | Cable 1kV 4c 2.5mm² Cu BVX4DCV:
5.1.1 |  | Supply, install, testing and terminate. | m | 1500 |  |  | 0
5.2.1 | D-DT-3128 | Cable 1kV 4c 4mm² Cu BVX4ECV:
5.2.1 |  | Supply, install, testing and terminate. | m | 3000 |  |  | 0
5.3 | D-DT-3128 | Cable 1kV 12c 2.5mm² Cu BVX12DCV:
5.3.1 |  | Supply, install, testing and terminate. | m | 900 |  |  | 0
5.4 | D-DT-3128 | Cable 1kV 12c 4mm² Cu BVX12ECV:
5.4.1 |  | Supply, install, testing and terminate. | m | 600 |  |  | 0
5.5 | D-DT-3128 | Cable 1kV 19c 2.5mm² Cu BVX19DCV:
5.5.1 |  | Supply, install, testing and terminate. | m | 900 |  |  | 0
5.6 | D-DT-3128 | Cable 1kV 19c 4mm² Cu BVX19ECV:
5.6.1 |  | Supply, install, testing and terminate. | m | 300 |  |  | 0
5.7 | D-DT-3128 | Cable 1kV 4c 25mm² Cu BVX4KCV:
5.7.1 |  | Supply, install, testing and terminate. | m | 300 |  |  | 0
5.8 |  | RED & BLACK Jumper Wire 200m roll -Contact 011 8542349:
5.8.1 |  | Supply, install, testing and terminate. | no | 4 |  |  | 0
5.9 | D-DT-9161 | Cable telephone 50pr 0.5mm dia (unarmoured: )
5.9.1 |  | Supply, install, testing and terminate. | no | 65 |  |  | 0
5.10 | D-DT-9161 | Cable telephone 25pr 0.5mm dia (unarmoured: ):
5.10.1 |  | Supply, install, testing and terminate. | no | 65 |  |  | 0
5.11 | D-DT-9161 | Cable telephone 10pr 0.5mm dia (unarmoured: )
5.11.1 |  | Supply, install, testing and terminate. | no | 65 |  |  | 0
5.12 |  | Krone Blocks - 10 block:
5.12.1 |  | Supply, prepare and install. | no | 2 |  |  | 0
5.13 | 240-64100247 | EAK Earth kits No.2:
5.13.1 |  | Supply, prepare and install. | no | 2 |  |  | 0
5.14 | 240-64100247 | EAK Earth kits No.1:
5.14.1 |  | Supply, prepare and install. | no | 4 |  |  | 0
5.15 |  | Trunking CLT/6 100x100x3m grey:
5.15.1 |  | Supply, prepare and install. | m | 10 |  |  | 0
5.16 |  | 40mm gret PVC Conduit 25m per Roll:
5.16.1 |  | Supply, prepare and install. | no | 2 |  |  | 0
5.17 | 240-56227443 | 300mm Cabe Trays (galvanised steel wire) in trenches for Control Cable ( Baskets type):
5.17.1 |  | Supply, prepare and install. | m | 20 |  |  | 0
5.18 | 240-56227443 | Cat 6 Ethernet Network Cable
5.18.1 |  | Supply, prepare and install. | m | 250 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Secondary Plant 2
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C5 |  | Secondary Plant (Continued) Balance B/F |  |  |  |  | 0
5.18 | D-DT-3070 | BVX 4 HCV Gland No 2 & Shroud + earth ring:
5.18.1 |  | Supply, prepare and install. | no | 0 |  |  | 0
5.19 |  | BVX 4 DCV Gland No 1 & Shroud + earth ring:
5.19.1 |  | Supply, prepare and install. | no | 40 |  |  | 0
5.20 |  | BVX 4 ECV Gland No 1 & Shroud + earth ring:
5.20.1 |  | Supply, prepare and install. | no | 86 |  |  | 0
5.21 |  | BVX 12 DCV Gland No 2 & Shroud + earth ring:
5.21.1 |  | Supply, prepare and install. | no | 40 |  |  | 0
5.22 |  | BVX 12 ECV Gland No 3 & Shroud + earth ring:
5.22.1 |  | Supply, prepare and install. | no | 10 |  |  | 0
5.23 |  | BVX 19 DCV Gland No 2 & Shroud + earth ring:
5.23.1 |  | Supply, prepare and install. | no | 18 |  |  | 0
5.24 |  | BVX 19 ECV Gland No 3 & Shroud + earth ring:
5.24.1 |  | Supply, prepare and install. | no | 4 |  |  | 0
5.25 |  | BVX 4 KCV Gland No 3 & Shroud + earth ring:
5.25.1 |  | Supply, prepare and install. | no | 6 |  |  | 0
5.26 |  | All Cable Terminals,grey wire, cable ties, core numbering, Tags and Ferrules as per Design drawings:
5.26.1 |  | Supply, prepare and install. | sum | 1 |  |  | 0
5.27 |  | VT JB -VRW20 Junction Box, with 8 circuit, including VT insert. (Fitted) (COMPLETE JB) (304 Stainless).:
5.27.1 |  | Supply and install. | no | 0 |  |  | 0
5.28 |  | Isolator JB - VRW20 Junction Box, with double busbar isolator including insert CT and VT tray. (Fitted) (COMPLETE JB) (304 Stainless):
5.28.1 |  | Supply and install. | no | 2 |  |  | 0
5.29 |  | CT JB -VRW20 Junction Box, with 6 circuit including CT insert. (Fitted) (COMPLETE JB) (304 Stainless):
5.29.1 |  | Supply and install. | no | 1 |  |  | 0
5.30 | D-DT-15207 | 5TM3100 - 132/22kV transformer protection scheme 110V/1A - Including (Sap no. 3000031095; 3000031098;3000028145;3000031189;0000701933;0000701696;0000701870;0000701874;0000701698;0000701702;0000701725(x2);0000701726;0000701876 ). Relays (RET670, REF615, REGDA)- Refer to transformer specification for detailed ordering options.Contract 4600071130
5.30.1 |  | Design, supply and install. | no | 1 |  |  | 0
5.31 | D-DT-5400 | Swing frame panel 2400(h) x 800(w) x 600(d):
5.31.1 |  | Supply and install. | no | 1 |  |  | 0
5.32 | D-DT-5416 | 5JB-3200 Transformer PIU Schemec- Refer to specification for detailed ordering options:
5.32.1 |  | Design, supply and install. | no | 1 |  |  | 0
5.33 |  | FAT of offered Protection Scheme
5.33.1 |  | Testing | no | 1 |  |  | 0
5.34 |  | Daily Rate for Installation Supervision
5.34.1 |  | Supervise | Days | 21 |  |  | 0
5.35 |  | Complete Installation, testing and commisioning of complete Feeders and transformers by Contractor ( Excludes 5JB-3200 & 5TM3100 schemes)
5.35.1 |  | Install, testing and commission | sum | 1 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Secondary Plant 3
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C5 |  | Secondary Plant (Continued) Balance B/F |  |  |  |  | 0
5.36 | D-DT-5408 | 11kV 2500A Vacuum circuit breaker panels- Bus section Controller Refer to detailed ordering schedule ( As per ordering options SBV3s) - Bus Section No.2:
5.36.1 |  | Supply and install. ( Including rigging of panels into the switchroom) | no | 1 |  |  | 0
5.37 | D-DT-5408 | 11kV 2500A Vacuum circuit breaker panels with Voltage Transformer- Refer to detailed ordering schedule ( As per ordering options SBV3s) - Transformer No.3:
5.37.1 |  | Supply and install. ( Including rigging of panels into the switchroom) | no | 1 |  |  | 0
5.38 | D-DT-5408 | 11kV 2500A Vacuum circuit breaker panels SBV3s with integrated Cable Feeder Protection Scheme - 3CF-4100F (With SolkorN ) - Refer to detailed ordering schedule - Feeder no.15 and no.16:
5.38.1 |  | Supply and install. ( Including rigging of panels into the switchroom) | no | 2 |  |  | 0
5.39 |  | FAT and SAT Testing of all protection panels ( Complete FAT and SAT testing with results and Includes Flights and accomodation for Engineer, Eskom and client):
5.39.1 |  | FAT and SAT Testing. | sum | 1 |  |  | 0
5.40 |  | All Protection Coordination and Relay settings complete:
5.40.1 |  | Coordination and settings. | sum | 1 |  |  | 0
5.41 |  | Testing and pre-commissioning of primary plant equipment and all protection systems (11kV Switchbord) :
5.41.1 |  | Testing and pre-commissioning. | sum | 1 |  |  | 0
5.42 | D-DT-9400 | Measurements (Sub panel Meter module) - Stats:
5.42.1 |  | Supply and install. | no | 1 |  |  | 0
5.43 | D-DT-9121 | ZMD Digital transducer -ENC 4600002391. According to Eskom drawing D-DT-9121:
5.43.1 |  | Supply and install. | no | 1 |  |  | 0
5.44 | D-DT-9420 | Meter,ZMD Landis & Gyr, A1700 3PH 1A , Class 0.5, RS232,485:
5.44.1 |  | Supply and install. | no | 1 |  |  | 0
5.45 | D-DT-9407 | Vectograph by CT Lab (Alternately Vecto 3 if Vectograph not available) as per Eskom Standard:
5.45.1 |  | Supply and install. | no | 1 |  |  | 0
5.46 | D-DT-9403 | Quality of Supply - AC Aux and Vectograph module
5.46.1 |  | Supply and install. | no | 1 |  |  | 0
5.47 |  | 3U Plates
5.47.1 |  | Supply and install. | no | 2 |  |  | 0
5.48 |  | All ancillaries and accessories to ensure function operation.
5.48.1 |  | Supply and install. | sum | 1 |  |  | 0
5.49 |  | All Metering
5.49.1 |  | Testing and Commissioning | sum | 1 |  |  | 0
5.50 | D-DT-9023 | ARC SENSOR, ARC SCHEME INCL 6M(20M) LEAD D9023
5.50.1 |  | Supply and install. | no | 14 |  |  | 0
5.51 | D-DT-9023 | RELAY, TRIP RELAY(AR112-2112J029) D9023
5.51.1 |  | Supply and install. | no | 3 |  |  | 0
5.52 | D-DT-9023 | RELAY, SLAVE UNIT(VAMP125) D9023
5.52.1 |  | Supply and install. | no | 2 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Secondary Plant 4
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C5 |  | Secondary Plant (Continued) Balance B/F |  |  |  |  | 0
5.53 | D-DT-9049 | Current transformer test block (PK2-4way) -IST
5.52.1 |  | Supply and install. | no | 1 |  |  | 0
5.54 | D-DT-5408 | Diode Terminal (M4/6 SNB) Entrelec:
5.54.1 |  | Supply and install. | no | 1 |  |  | 0
5.55 |  | All accessories, wiring and ancillaries to modify and ensure functionality (132kV & 11kV Buszone) :
5.55.1 |  | Supply and install. | sum | 1 |  |  | 0
5.56 |  | 132kV Buszone Integration with transformer no.3 scheme.All material necessary to integrate the equipment shall be part of the rate:
5.56.1 |  | Supply and install. | sum | 1 |  |  | 0
5.57 | 240-53114248 | Battery Charger 110V 20A 3Ph CVC, CXC HP, 1xTypeC in S/F. Stock code ; 3V11020/CE001:
5.57.1 |  | Supply and install. | no | 1 |  |  | 0
5.58 |  | Ethernet cable for remote communication:
5.58.1 |  | Supply and install. | no | 1 |  |  | 0
5.59 | 217242CE | 110V Rectifiers Modules - 1.1kw (To achieve a 30A Charger) :
5.59.1 |  | Supply and install. | no | 1 |  |  | 0
5.60 |  | 1) 52x CELL, BATTERY: TYPE: WET, FLAT PLATE; POTENTIAL: 2 V; CAPACITY: 170 AH; DIMENSIONS: WD 208 X LG 105 X HT 420 MM; STANDARD: 240-56360034 REV 3; WEIGHT:16,7KG. C10 RATING AT 25 DEG C TO 1,8V/CELL: 170AH. INCLUDES 1 AQUAGEN PRO RECOMBINATION UNIT; DRAWING NO: 9224; PART NO: V M 2-170W; VENDORS ARE RESPONSIBLE FOR ENSURING THAT THEY ARE PERFORMING AGAINST THE CORRECT DRAWING REVISION NUMBER (IF APPLICABLE). 2) 1x CONNECTOR, ELECTRICAL: TYPE: CELL INTER-ROW TYPE 1; DIMENSIONS: DIA 90 MM2 X LG 200 MM; SUITABLE FOR USE ON BATTERY STANDS WITH THE FOLLOWING PLANTÉ / FLAT PLATE CELLS VM 2 -125, VM 2 -170, VM 2 -210, VX 2 -75, VX 2 -100, VX 2 -125, VX 2 -150; DRAWING NO: 9226; VENDORS ARE RESPONSIBLE FOR ENSURING THAT THEY ARE PERFORMING AGAINST THE CORRECT DRAWING REVISION NUMBER (IF APPLICABLE). 3) 1x DEVICE: TYPE: BATTERY TERMINATING, TYPE 1; SUITABLE FOR USE ON BATTERY STANDS WITH THE FOLLOWING PLANTÉ / FLAT PLATE CELLS:VM 2 -125, VM 2 -170, VM 2 -210, VX 2 -75, VX 2 -100, VX 2 -125, VX 2 -150 ; DRAWING NO: 9226; VENDORS ARE RESPONSIBLE FOR ENSURING THAT THEY ARE PERFORMING AGAINST THE CORRECT DRAWING REVISION NUMBER (IF APPLICABLE). 4) 1x STAND, BATTERY: TYPE: FLAT PLATE,52 C,RANGE 1,DRST; SIZE: WD 500 X LG 2990 X HT 780 MM; MATERIAL: LAMINATED PINE; STANDARD: 240-56360034 REV 3; SUITABLE FOR 52 OF THE FOLLOWING FLAT PLATE CELLS:V M 2-125, V M 2-170, V M 2-210; DRAWING NO: 9225; VENDORS ARE RESPONSIBLE FOR ENSURING THAT THEY ARE PERFORMING AGAINST THE CORRECT DRAWING REVISION NUMBER (IF APPLICABLE).
5.60.1 |  | Supply and install. | sum | 1 |  |  | 0
5.61 |  | Swing AC and DC Cable and Decommissioning old Lead Acid cells and transporting to eskom stores :
5.61.1 |  | Swing Cables, Decommissioning and Transportation | sum | 1 |  |  | 0
5.62 |  | Maintenance & safety equipment rack for Lead Acid batteries, including jug, funnel, eye-wash bottle, face shield, apron, top-up bottle and rubber gloves:
5.62.1 |  | Maintenance and safety | sum | 1 |  |  | 0
5.63 |  | Testing and Commissioning of Battery charger and cells and providing discharge results:
5.63.1 |  | Testing and Commissioning | sum | 1 |  |  | 0
5.64 |  | All accessories and ancillaries to ensure functionality (Battery Charger and Cells):
5.64.1 |  | Functionality ensurance | sum | 1 |  |  | 0
5.65 |  | FAT and SAT Testing of battery charger ( Complete FAT and SAT testing with results and Includes Flights and accomodation for Engineer, Eskom and client):
5.65.1 |  | FAT and SAT Testing | sum | 1 |  |  | 0
5.66 | D-DT-11201 | Yard Change over AC Board without distribution (Includes control module, single and dual, distribution modeule and termination module with steel structure and automatic transfer switch)
5.66.1 |  | Supply and install. | no | 1 |  |  | 0
5.67 |  | Testing and issuing of (a) Compliance Certificate(s) in accordance to SANS 10142-1 for the Transformer Juction Boxes, Yard Lights and Yard AC Distribution Board, for the AC & DC Distribution Boards and electrical installation in the Control Room, etc.
5.67.1 |  | Testing and issuing of (a) Compliance Certificate(s) | no | 1 |  |  | 0
5.68 |  | Supply and install a 3 Phase AC Module onto existing AC Panel:
5.68.1 |  | Supply and install. | no | 1 |  |  | 0
5.69 |  | Chequer plate: Cut to size, touch up paintwork where needed and fit (For the control building):
5.69.1 |  | Prepare and modify where needed. | sum | 1 |  |  | 0
|  | Balance C/F |  |  |  |  | 0

## Secondary Plant 5
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C5 |  | Secondary Plant (Continued) Balance B/F |  |  |  |  | 0
5.70 |  | Testing and pre-commissioning of primary plant equipment and all protection systems ( Buszone and BusBars):
5.70.1 |  | Testing and pre-commissioning. | sum | 1 |  |  | 0
5.71 |  | Testing and pre-commissioning of D20 RTU telecontrol system::
5.71.1 |  | Testing and pre-commissioning. | sum | 1 |  |  | 0
5.72 |  | Testing and pre-commissioning of optic fibre system:
5.72.1 |  | Testing and pre-commissioning. | sum | 1 |  |  | 0
5.73 |  | Test and pre-commissioning of AC/DC Panel:
5.73.1 |  | Testing and pre-commissioning. | sum | 1 |  |  | 0
5.74 |  | Allow for final Hand-Over Certificate documentation:
5.74.1 |  | Final hand-over. | sum | 1 |  |  | 0
5.75 | 240-62629353 | control panel labels:
5.75.1 |  | Supply and install | sum | 1 |  |  | 0
5.76 | D-DT-9141 | 1U Blanking Plate:
5.76.1 |  | Supply and install. | no | 1 |  |  | 0
5.77 | D-DT-9141 | 2U Blanking Plate:
5.77.1 |  | Supply and install. | no | 2 |  |  | 0
5.78 | D-DT-9141 | 3U Blanking Plate:
5.78.1 |  | Supply and install. | no | 2 |  |  | 0
5.79 |  | Cage Nuts, Bolts With Sealing Washer 6mm :
5.79.1 |  | Supply and install. | no | 100 |  |  | 0
5.80 |  | Transportation of all control plant equipment and materials to site including crane to lift and install panels:
5.80.1 |  | Transportation. | sum | 1 |  |  | 0
|  | Total C5 |  |  |  |  | 0

## Fibre-Power Cabling
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Description of the item | Unit | Quantity | Material Rate | Labour Rate | Total Price
Rands
C6 |  | Fibre & Power Cabling
6.1 |  | 12 core 1310nm multi mode All Dielectric CST fibre (50/125um):
6.1.1 |  | Supply and install. | m | 300 |  |  | 0
6.2 |  | Heavy Duty Duct fibre 6 core 1310nm Multi Mode (50/125um):
6.2.1 |  | Supply and install. | m | 25 |  |  | 0
6.3 |  | 32mm Optex sub duct:
6.3.1 |  | Supply and install. | m | 300 |  |  | 0
6.4 |  | Fibe Optic Patch Box 2552A - by 3M ( For Transformer PIU Junction Box):
6.4.1 |  | Supply and install. | no | 2 |  |  | 0
6.5 |  | 6 Way ODF (Patch Panel):
6.5.1 |  | Supply and install. | no | 3 |  |  | 0
6.6 |  | 6 Way termination box :
6.6.1 |  | Supply and install. | no | 3 |  |  | 0
6.7 |  | 12 Core 1310nm 50/125um Duplex multimode Patch leads 3meter(ST/ST):
6.7.1 |  | Supply and install. | no | 6 |  |  | 0
6.8 |  | CAT6 Copper Ethernet Cable.
6.8.1 |  | Supply and install. | m | 200 |  |  | 0
6.9 |  | Cable Splicing (Including kit):
6.9.1 |  | Supply and install. | no | 25 |  |  | 0
6.1 |  | Terminal Kits, to include ST-ST connectors
6.10.1 |  | Supply and install. | sum | 1 |  |  | 0
6.11 |  | Testing Drum
6.11.1 |  | Testing and Commissioning | no | 1 |  |  | 0
6.12 |  | Test/Commissioning certificates. Results and project file
6.12.1 |  | Testing and Commissioning | sum | 1 |  |  | 0
6.13 |  | Meinberg Lantime M320 GPS Clock with cards and ancillaries LANTIME M320/GPS/TC-1-1/AD10 NTP Time Server incl. the following accessories: - 1 x GPSANTv2 (GPS antenna-/converter unit) - 1 x 20m antenna cable RG58 (N-Norm male / BNC male) - 1 x two part power cable kit - 1 x Accessory-kit (for LANTIME M300/M320) MBG S-PRO surge voltage protector (type: Phoenix CN-UB-280DC-BB) incl. the following accessories: - 1 x 5m antenna cable RG58 (N-Norm male / N-Norm male) HS-Code: 8536 3010 Power Supply: 100-240 V AC / 100-200 V DC (easily replaceable) Signal Outputs: 2 x LAN interface 10/100 MBit, RJ45 connector 2 x RS232 interface, independent, 9pin D-Sub female connector, with multi data formats timestrings. 1 x PPS, TTL into 50 ohm, pulse duration 200 msec, active high, female BNC connector 1 x Standard Frequency 10 MHz, TTL into 50 ohm, female BNC connector 1 x Alarm Relay Output, change-over contact, 3pin DFK connector 1 x Time Code AM, amplitude modulated sinewave output via female BNC connector 1 x Time Code DCLS, Pulse-width modulated output via female BNC connector - 1x LM-7000H Module Series
6.13.1 |  | Supply and install, test and commission | no. | 1 |  |  | 0
The supply & complete installation, testing and commissioning of all cabling, sleeves and terminations required to complete the power cabling of the substation, including the cabling from the auxiliary transformers at the earthing compensator units to the indoor distribution board, from this indoor distribution board to the substation distribution board, the control panels, the supervisory terminal box, switchgear, battery charger, floodlights, transformers and all other equipment where 400/231V 50Hz single or three phase power is to be available, including the installation of all glands and all terminations. Supply & delivery is included.
6.14 | D-DT-0854 | Trenching
6.14.1 |  | Supply and install | m³ | 300 |  |  | 0
6.15 | D-DT-0854 | Backfill and compaction
6.15.1 |  | Supply and install | m³ | 300 |  |  | 0
6.16 |  | 160mm dia. PVC sleeves
6.16,1 |  | Supply and install | m | 400 |  |  | 0
6.17 | D-DT 8001 | 11 kV 630mm² 1-core Cu XLPE From the cable end support to the indoor Transformer Incomer Panel
6.17.1 |  | Supply and install | m | 1700 |  |  | 0 | #N/A
6.18 | D-DT 8006 | 11 kV 630mm² 1-core Cu XLPE O/D and I/D termination
6.18.1 |  | Supply and Terminate | no | 24 |  |  | 0 | 0
6.19 | D-DT 8001 | 11 kV 95mm² 3-core Cu XLPE
6.19.1 |  | Supply and install | m | 100 |  |  | 0 | 0
6.20 | D-DT 8006 | 11 kV 95mm² 3-core Cu XLPE O/D and I/D termination
6.20.1 |  | Supply and Terminate | no | 6 |  |  | 0 | 0
6.21 |  | 50mm², 4-core, copper 600/1000V, PVC SWA cable
6.21.1 |  | Supply, install and Terminate | no | 150 |  |  | 0
6.22 |  | 16mm², 4-core, copper 600/1000V, PVC SWA cable
6.22.1 |  | Supply, install and Terminate | m | 100 |  |  | 0 | 0
6.23 |  | 4mm², 4-core, copper 600/1000V, PVC SWA cable
6.23.1 |  | Supply, install and Terminate | m | 300 |  |  | 0 | 0
6.24 |  | Power Cabling
6.24.1 |  | Testing and Commissioning | sum | 1 |  |  | 0 | 0
|  | Total C6 |  |  |  |  | 0

## Label Schedule
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
Item No. | Ref. DRG. No. Proj. Spec. | Rev | Label Designation | Label Description | Key Tag |  | Lock |  | Label Size | Qty
[5 empty] | Yes | No | Yes | No
Label Schedule
D-DT-5047
1 | Set 5 Sht 2 & 4 | 3 | TRFR 3 | 132 kV BUSBAR 1 ISOLATOR | √ | - | √ | - | 600 x 250 | 1
2 |  |  | TRFR 3 | 132 kV BUSBAR 2 ISOLATOR | √ | - | √ | - | 600 x 250 | 1
3 |  |  | TRFR 3 | 132 kV BKR | √ | - | √ | - | 600 x 250 | 1
4 |  |  | TRFR 3 | 132 kV CT | √ | - | √ | - | 600 x 250 | 3
5 |  |  | TRFR 3 | 132 kV CT JB | √ | - | √ | - | 600 x 250 | 1
6 |  |  | TRFR 3 | 132/11 kV | √ | - | √ | - | 600 x 250 | 1
7 |  |  | TRFR 3 | 11 kV /400 V NECRT 3 | √ |  | √ | - | 600 x 250 | 1
8 |  |  | TRFR 3 | 22 kV BUSBAR 1C ISOLATOR | √ | - | √ | - | 600 x 250 | 1
9 |  |  | 132 kV BUSBAR 1 |  | - | √ | - | √ | 1000 x 250 | 2
10 |  |  | 132 kV BUSBAR 2 |  | - | √ | - | √ | 1000 x 250 | 2
CIRCUIT BREAKER INDOOR
11 |  |  | TRFR 3 | 11 kV BKR | - | - | - | - | 35 x 150 | 1
12 |  |  | BUSBAR 1C | 11 kV VT | - | - | - | - | 35 x 150 | 1
13 |  |  | BUS-SECTION 2 | 11 kV BKR | - | - | - | - | 35 x 150 | 1
14 |  |  | IDZ FDR 15 | 11 kV BKR | - | - | - | - | 35 x 150 | 1
15 |  |  | IDZ FDR 16 | 11 kV BKR | - | - | - | - | 35 x 150 | 1

## App B 1
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
List all drawings applicable to the works or the asset and temporary works, indicating whether they are approved for use (ABU) or not.
Drawing No. | Rev | Title | AFU Att
Substation layout
D-EC-1973-1A | 5 | Station Electric Diagram | Yes
D-EC-1973-1B | 5 | Station Electric Diagram -Transformer 1 Incomer | Yes
D-EC-1973-1C | 4 | Station Electric Diagram -Transformer 2 Incomer | Yes
D-EC-1973-1D | 0 | Station Electric Diagram -Transformer 3 Incomer | Yes
D-EC-1973-2 | 1 | Site Plan & Future Extension | Yes
D-EC-1973-4 | 1 | Earthmat Layout | Yes
D-EC-1973-5 | 2 | Foundation layout | Yes
D-EC-1973-6 | 1 | Steelwork Layout | Yes
D-EC-1973-7 | 1 | Electrical Equipment Layout | Yes
D-EC-1973-8 | 1 | Sections & Clamps | Yes
D-EC-1973-9B | 0 | Transformer 3 Plinth Detail with Oil Catchment Area | Yes
D-EC-1973-11 | 0 | Oil Trap Details | Yes
D-EC-1973-12 | 1 | Trench & Fence Layout | Yes
D-EC-1973-20 | 0 | Yard Lighting Layout | No
D-EC-1973-21 | 0 | Lightning Protection Layout | No
D-EC-1735-1 | 4 | Precast Concrete 750mm Trench Cover | Yes
D-EC-1735-2 | 2 | Precast Concrete 1500mm Trench Cover | Yes
Control Building
D-EC-1973-13 | 1 | Control Building Detail Plan Section and Elevations | Yes
D-EC-1973-14 | 2 | Control Building Electrical Layout | Yes
D-EC-1973-15 | 1 | Control Building Door, Window Schedule and Detail | Yes
D-EC-1973-16 | 1 | Control Building Section and Specifications | Yes
D-EC-1973-17 | 1 | Control Building Trench Cover Layout and Details | Yes
D-EC-1973-18 | 2 | Control Building Distribution Board and Sub-Distribution Board Diagrams | Yes
D-EC-1973-19 | 1 | Control Building Typical Detail of Ducting Entry into Building | Yes
D-SR-121-03 | 1 | Control Building Switchgear Room and Relay Room Panel Arrangement | Yes
Equipment Foundations
D-EC-1974-1 | 0 | Road Crossing Support Foundation Details | Yes
D-DT-5220-1A | 9 | Tubular Busbar - 132kV 3m Phase CRS Single Tubular Support Foundation Details | Yes
D-DT-5200-1A | 9 | Circuit breaker - 132kV Tubular support foundation details - cable pipe | Yes
D-DT-5202-1A | 14 | Isolator - 132kV 3 & 3.6m phase CRS Lattice support foundation details | Yes
D-DT-5206-1A | 9 | Medium equipment lattice support foundation details | Yes
D-DT-5217-1B | 6 | Lighting - lightning mast - 14m Tubular support foundation details | Yes
D-DT-5207-1A | 2 | NECR'T/ AUX.TRFR 6.6-22kV Lattice Support Foundation Details | Yes
D-DT-5205-1A | 9 | Isolator - 22kV 1m Phase CRS Lattice Support Foundation Details | Yes
D-DT-5213-1A | 10 | MV Cable Sealing End Lattice Support Foundation Details | Yes
D-DT-5416-22 | 0 | PIU (5JB-3200) Plinth Detail | Yes
Trenching 750/1500mm
D-DT-5254-1A | 0 | Trench Cover - 750mm | Yes
D-DT-5254-1B | 0 | Trench Cover - 1500mm | Yes
D-DT-5254-2A | 0 | Trench Kerbing - 1000mm (Concrete) | Yes
D-DT-5254-2C | 0 | Stone Kerbing - 1000mm (Concrete) | Yes
D-DT-5254-3E | 0 | LV Cable Road Duct 10 - Pipe | Yes
D-DT-5254-5A | 0 | Trench 750mm Wide - Straight | Yes
D-DT-5254-5B | 0 | Trench 1500mm Wide - Straight | Yes
D-DT-5254-5F | 0 | Trench 1500mm Wide - 90 ˚ Type 'A' Bend Installation and Sections | Yes
D-DT-5254-5I | 0 | Trench 750mm Wide - 'T' To 1500mm wide Straight Installation and Sections | Yes
D-DT-5254-6A | 0 | Trench - 750mm Trench Cover Support Manufacturing Details | Yes
D-DT-5254-6B | 0 | Trench - 1500mm Trench Cover Support Manufacturing Details | Yes
Equipment Steelwork
D-EC-1974-2 | 0 | Road Crossing Support Steelwork Manufacturing Details and Assembly | Yes
D-DT-5200-2A | 13 | Circuit breaker - 132kV Tubular support steelwork manufacturing details | Yes
D-DT-5202-2A | 17 | Isolator STD - 123kV Manual lattice support steelwork manufacturing details and assembly | Yes
D-DT-5202-2I | 2 | Isolator Inline - 123kV Manual lattice support steelwork manufacturing details and assembly | Yes
D-DT-5206-2C | 9 | Medium equipment - 2.5m Lattice support steelwork manufacturing details and assembly | Yes
D-DT-5206-2H | 7 | Medium equipment - Cap M1 Channel support steelwork manufacturing details and assembly | Yes
D-DT-5217-2B | 11 | Lighting - lightning mast - 14m Tubular support steelwork manufacturing details and assembly | Yes
D-DT-5220-2 | 11 | 132kV Tubular Busbar Support Details | Yes
D-DT-5207-2A | 12 | NECR'T/AUX.TRFR 6.6-22kV LATICE SUPPORT-0.4 & 1.5m Steelwork Manufacturing Details | Yes
D-DT-5205-2A | 9 | Isolator STD - 22kV Manual Lattice Support Steelwork Manufacturing Details and Assembly - 1m Phase CRS | Yes
D-DT-5219-1 | 3 | Surge Arrestor Bracket 11/22kV Mounted on Isolator Support | Yes
D-DT-5213-2D | 1 | MV Cable End Support 2 OR 4 x Single Core Cable/Phase Lattice Support SteelWork Manufacturing Details and Assembly | Yes
D-DT-5416-22 | 0 | PIU Steelwork Assembly | Yes

## App B 2
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
List all drawings applicable to the works or the asset and temporary works, indicating whether they are approved for use (ABU) or not.
Drawing No. | Rev | Title | AFU Att
Support Brackets & Signage
D-DT-3207-1 | 3 | Bracket, Cable Termination Support Bracket, Galvanised | Yes
D-DT-8013-1 | 5 | BRACKET, PHASE COLOUR DISC | Yes
D-DT-6114-1 | 5 | PLATE, PH MKR RED W/BLK R - Chromadek | Yes
D-DT-6114-1 | 5 | PLATE, PH MKR BLU W/BLK B - Chromadek | Yes
D-DT-6114-1 | 5 | PLATE, PH MKR WHT W/BLK W - Chromadek | Yes
Labels
D-DT-5047 | 3 | Electrical equipment label details | Yes
Equipment Specification (Outdoor Plant)
D-DT-6230-1 | 7 | INSUL:STN POST;C4-550;132 KV | Yes
D-DT-6302-1 | 5 | ISO,EL:132 KV ;2500 A ;40 KA ;HAND ;0ES | Yes
D-DT-6302-4 | 5 | ISO,EL:132 KV ;2500 A ;40 KA ;INLHAND | Yes
D-DT-6250-1 | 14 | BKR:LT;132 KV;3150 A;40 KA;3;110 VDC | Yes
D-DT-6190-1 | 11 | CT 132kV 2500A 40kA 2P2M2B1600 31 | Yes
D-DT-6210-1 | 10 | S/ARR S/CL 132kV MCOV 84kV 31 | Yes
D-DT-6120-2 | 8 | TRFR 40MVA 132/11kV OLTC (SI) YNd1 31 | Yes
D-DT-6216-1 | 10 | S/ARR S/CL 11kV MCOV 12kV | Yes
D-DT-6140-1 | 10 | NEC/NER/AUX TFR 11kV 360A 31 | Yes
D-DT-6305-1 | 3 | ISO:22 KV;2500 A;31.5 KA;H/O;0ES;110 VDC | Yes
D-DT-6009-1 | 1 | FLDLIGHT:LED;ALUMINIUM;60 W;7200 LM;FLT | Yes
D-DT-6232-1 | 7 | INSUL:STN POST;C4-325;66 KV | Yes
D-DT-5416 | 0 | PIU (5JB-3200) | Yes
Equipment Specification ( Indoor Breaker Panel)
D-DT-6258-3 | 7 | 11kV Incomer Breaker Panel 2500A 25kA | Yes
D-DT-6258-3 | 7 | 11kV Bus-Section Breaker Panel 2500A 25kA | Yes
D-DT-6258-3 | 7 | 11kV Feeder Breaker Panel 2500A 25kA | Yes
D-DT-6175-2 | 11 | 11kV VT 11kV/110 50VA cl0.2 (2500A) BUSBAR | Yes
|  | 11kV CT 2500A 25kA 2P PX FDR | Yes
|  | 11kV CT 2500A 25kA 3P PX TRFR | Yes
Earthing
D-DT-6044-1 | 5 | 10mmØ Round Copper Bar | Yes
D-DT-6045-1 | 4 | 50mm x 3mm Flat Copper Bar | Yes
D-DT-5240-5 | 3 | Strip galvanised steel 6 x 80mm | Yes
D-DT-6366-1 | 0 | 26mm dia Yard stone | Yes
HD Bolts
D-DT-3015-5 | 27 | Rod, Threaded Galv M24x350mm Wash+Nuts | Yes
D-DT-3015-5 | 27 | Rod, Threaded Galv M24x500mm Wash+Nuts | Yes
D-DT-3015-6 | 27 | Rod, Threaded Galv M24x1000mm Wash+Nuts | Yes
|  | Rod, Threaded Galv M30x400mm Wash+Nuts | Yes
Conductor and Cable Specification
D-DT 3136-8 | 13 | COND, AAC HORNET 16.25D INSU UNGRS | Yes
D-DT 3136-8 | 13 | COND, AAC CENTIPEDE 26.45D INSU UNGRS | Yes
D-DT 3136-8 | 13 | COND, AAC BULL 38.25D INSU UNGRS | Yes
D-DT 3136-7 | 13 | COND, AAC BULL 38.25D UNGRS | Yes
D-DT 8001-2 | 14 | 11 kV 630mm² 1-core Cu XLPE | Yes
D-DT 8006-8 | 15 | 11 kV 630mm² 1-core Cu XLPE O/D termination | Yes
D-DT 8006-8 | 15 | 11 kV 630mm² 1-core Cu XLPE I/D termination | Yes
D-DT 8001-1 | 14 | 11 kV 95mm² 3-core Cu XLPE | Yes
D-DT 8006-27 | 15 | 11 kV 95mm² 3-core Cu XLPE O/D termination | Yes
D-DT-8006-27 | 15 | 12 kV 95mm² 3-core Cu XLPE I/D termination | Yes
D-DT 6000-1 | 5 | TUBE :BUSBAR; LG 12M;OD 120mm; ID 112mm | Yes
Stranded and Tubular Conductor Clamps Specification
D-DT-3074-2 | 8 | LUG,AL HORNET 1B M12 0 DEG I/C | Yes
D-DT-6109-2 | 7 | CLAMP:EYC-T;COMP/PALM 90DG;2X38.3 MM | Yes
D-DT-6002-2 | 6 | CLAMP:EX-C;BOLT/BOLT; STEM 38 COND 16.3 | Yes
D-DT-6115-1 | 2 | CLAMP, PEG AL BULL 38.3mm EPC-38 | Yes
D-DT-6002-2 | 6 | CLAMP:EX-D;BOLT/BOLT; STEM 38 COND 26.5 | Yes
D-DT-6002-2 | 6 | CLAMP:EX-B;BOLT/BOLT; STEM 26 COND 26.5 | Yes
D-DT-6013-2 | 10 | CLAMP:EYC-B;2X38.3 COMP 38 BOLTED 0DG | Yes
D-DT-6006-2 | 9 | CLAMP:EXC-C;BOLT/COMP; STEM 38 COND38.3 | Yes
D-DT-6002-2 | 6 | CLAMP:EX-E;BOLT/BOLT; STEM 38 COND 38.3 | Yes
D-DT-6018-3 | 8 | CLAMP:EPC-D;COMP/PALM ODG;38.3 MM | Yes
D-DT-6018-3 | 8 | CLAMP:EPC-E;COMP/PALM 45DG;38.3 MM | Yes
D-DT-6029-2 | 6 | CLAMP:EXCP-D;PI MOUNT;38.3 MM;PCD 127 | Yes
D-DT-6018-3 | 8 | CLAMP:EPC-F;COMP/PALM 90DG;38.3MM | Yes
D-DT-6081-1 | 8 | JOINT, BALL PORTABLE EARTH 20kA G/S | Yes
D-DT-6090-6 | 8 | CLAMP,TUBE:ETP-TE-IL2-R;120/2X38.3;0D | Yes
D-DT-6040-5 | 6 | CLAMP,TUBE:ETEC-DC-C;120/4;38.3C-ENDCAP | Yes
D-DT-6040-2 | 6 | CLAMP,TUBE:ETEC-PL-C;120/4;PLAIN- ENDCAP | Yes
D-DT-6000-1 | 5 | TUBE:BUSBAR;LG 12 M;OD 120 MM;ID 112 MM | Yes
D-DT-6039-2 | 8 | CLAMP,TUBE:ESC-PI-F-F;120/127;FIXED | Yes
D-DT-6316-2 | 2 | CLAMP,TUBE:ESC-PI-S-F;120/127;SLIDE | Yes
D-DT-6119-2 | 4 | CLAMP,TUBE:ETP-IL1-J;120/38.3;SINGLE | Yes
D-DT-6117-1 | 3 | CLAMP,TUB BUS/PALM T/OFF TBPT120 | Yes

## 11kV Board Spec.
Bill of Quantities: Leaches Bay S/S UPGRADE : 132/11kV TRFR 3 BAY
MV SWITCHGEAR |  |  |  | DESCRIPTION | 4 X SBV3S EXT PANELS IDZ - EAST LONDON |  |  |  | SPECIFICATION |  | ES62493 REV 1
MAIN BOARD LABEL |  |  | Leaches Bay SS: EXTENSION |  |  | COLOUR | VARIES
|  |  | WIDTH |  |  | 2 OFF | 600mm |  | 2OFF | 800mm
VOLTAGE:- |  | 11KV
FAULT LEVEL:- |  | 25KA | PANEL LABEL |  | TRFR. 3 | TRANSFER FEEDER PANEL 15 |  | BUS-SECTION 2 |  | TRANSFER FEEDER PANEL 16
INTERNAL ARC |  | 0.2s
IMPULSE LEVEL:- |  | 95KVip
BUSBAR RATING |  |  |  | 2500A
CIRCUIT BREAKER/SWITCH | TYPE |  |  |  | SBV3S | SBV3S |  | SBV3S |  | SBV3S
| MEDIUM |  |  |  | VACUUM | VACUUM |  | VACUUM |  | VACUUM
| CURRENT RATING |  |  |  | 2400A | 2400A |  | 2400A |  | 2400A
| MECHANISM |  |  |  | M.W.S. | M.W.S. |  | M.W.S. |  | M.W.S.
HRC STRIKER PIN FUSES
| MOTOR/CONTACTOR VOLTAGE |  |  |  | 110VDC | 110VDC |  | 110VDC |  | 110VDC
| SHUNT TRIP COIL |  |  |  | 110VDC | 110VDC |  | 110VDC |  | 110VDC
| SPRING RELEASE COIL |  |  |  | 110VDC | 110VDC |  | 110VDC |  | 110VDC
UNDERVOLTAGE
| RACKING SWITCH |  |  |  | YES | YES |  | YES |  | YES
| SPARE AUX. CONTACTS |  |  |  | 6 N/O & 6 N/C | 6 N/O & 6 N/C |  | 6 N/O & 6 N/C |  | 6 N/O & 6 N/C
| INTERGRAL CABLE EARTH |  |  |  | CABLE | CABLE |  |  |  | CABLE
| MECHANICAL INTERLOCKING FOR BB EARTHING |  |  |  | YES | YES |  | YES |  | YES
| BUSBAR EARTHING |  |  |  | CABLE AND EARTH TRUCK | YES - SEPARATE ATTACHMENT
| COLOUR OF PANEL |  |  |  | G29 GREY | G29 GREY |  | ORANGE |  | G29 GREY
INSTRUMENT PANEL EQUIP | CONTROL SWITCH |  |  |  |  | T/N/C |  | T/N/C |  | T/N/C
| SELECTOR SWITCH |  |  |  |  | LOCAL/REMOTE |  | LOCAL/REMOTE |  | LOCAL/REMOTE
| REMOTE TRIP CLOSE SOCKET |  |  |  |  | SCAME |  | SCAME |  | SCAME
| LAMP TEST PUSHBUTTON |  |  |  | BLACK | BLACK |  | BLACK |  | BLACK
| INDICATION LED'S - OPEN/CLOSE |  |  |  | GREEN/RED | GREEN/RED |  | GREEN/RED |  | GREEN/RED
| CABLE EARTHED LED |  |  |  | AMBER | AMBER |  | AMBER |  | AMBER
| ITT PLUG |  |  |  | Yes | Yes |  | Yes |  | Yes
| PANEL HEATERS (CABLE/BUSBAR) + SWITCH |  |  |  | 220V AC | 220V AC |  | 220V AC |  | 220V AC
NEON INDICATION
INSTRUMENTS
| M.D.I AMMETER |  |  |  | 1 x 0-2400A | 1 x 0-2400A |  |  |  | 2 x 0-2400A
| AMMETER SELECTOR SWITCH |  |  |  | YES | YES |  |  |  | YES
LOOSE SCALES
VOLTMETER
VOLTMETER SELECTOR SWITCH
POWER QUALITY METER
| CURRENT TRANSDUCERS |  |  |  | YES - CA7 | YES - CA7 |  |  |  | YES - CA7
VOLTAGE TRANSDUCERS
KW TRANSDUCER
ENERGY METER
RELAYS | PROTECTION ESKOM |  |  |  |  | 3CF-4100F ONBOARD SCHEME EXCLUDING INCLUDING DIFFERENTIAL PROTECTION |  |  |  | 3CF-4100F ONBOARD SCHEME EXCLUDING INCLUDING DIFFERENTIAL PROTECTION
TRIP SUPERVISION
PILOT WIRE
VOLTAGE SELECTION RELAY
| ARC PROTECTION (Vamp) |  |  |  | Intergrated in 3BP-4901 | Intergrated in 3BP-4901 |  | Intergrated in 3BP-4901 |  | Intergrated in 3BP-490
TEST BLOCK DIFFERENTIAL
| TEST BLOCK PROTECTION |  |  |  |  | 1 x C & H 13 WAY |  |  |  | 1 x C & H 13 WAY
| TEST BLOCK METERING |  |  |  |  | 1 x C & H 13 WAY |  |  |  | 1 x C & H 13 WAY
VT'S |  |  | RATIO |  | 110000-110V
|  |  | BRD+ACC |  | 50VA Class 0.2
LOCATION
CT'S
| DIFFERENTIAL CLASS X |  |  |  | 1 X 2400/1 MR
| PROTECTION CLASS X |  |  |  | 1 X 2400/1 MR | 2 X 2400/1 MR |  |  |  | 2 X 2400/1 MR
| METERING CLASS 0.2 |  |  |  | 1 X 2400/1 MR | 1 X 2400/1 MR |  |  |  | 1 X 2400/1 MR
SUMMATION CLASS 0.2 10VA
CABLES | POWER CABLE ENTRY |  |  |  | BOTTOM | BOTTOM |  |  |  | BOTTOM
| TERMINATION |  |  |  | GLAND | GLAND |  |  |  | GLAND
| CLAMP/GLAND/COMPOUND |  |  |  | POLY PROP | POLY PROP |  |  |  | POLY PROP
| QUANTITY No/CORES/SIZE |  |  |  | 12x 1C 630mm² | 12x 1C 630mm² |  |  |  | 12x 1C 630mm²
| CABLE TYPE (PILC-PEX) |  |  |  | XLPE | XLPE |  |  |  | XLPE
| SURGE ARRESTOR |  |  |  | YES | YES |  |  |  | YES
| COMPILED | CD
| CHECKED | CD
| DATE | 2023-02-24

## Data (hidden)
*Note all fields highlighted in yellow contain a formalae and is not to be changed.
All white fields is where the the qauntities are entered.
All green is specific to a substation
Dgn no. | Description | Qauntity |  | Area | Excavations | Concrete | Cemetile prod. | Formwork | H.D. Bolts | H.D. Bolts | reinforcing kg | round cu | Bricks
[5 empty] | m3 | m3 | kg | m2 | kg | no. | kg | m
Isolators
D-DT-5205 S1 R3 | 22kV Isolator | 0 |  | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A
D-DT-5203 Sht 1 Rev 2 | 66kV isolator | 0 |  | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A
Circuit breakers
0.54/4246 rev. 0 | 88kV A.E.G Circuit breaker foundation | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A
0.54/534 rev. 5 | 66kV Reyrolle type OSM O.C.B | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A
0.54/4276 rev. 0 | 22kV GEC CB (dog box) | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A
D-DT-5200 s1 r1 | 132kV circuit bkr (soil type 1&2) | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
D-DT-5201 r1 | 66kV circuit bkr (soil type 1&2) | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other foundations
D-EC-1929 | 3m Container foundation | 0 |  | 0 | 0 | 0 | N/A | 0 | N/A | N/A | 0 | N/A
D-EC-1930 | Transformer supp fdn details | 0 |  | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | N/A
D-EC-1814 S1 | Auto recloser supporrt foundation | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
D-DT-5206 S1 R1 | Medium equipment supp. foundation | 1 |  | 0.81 | 0.6885 | 0.81 |  | 0.54 | 8.68 | 4
0.54/329 | Column foundation | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
D-DT-5051-1 | Standard lighting/lightning spike foundattion 8m type 'B' | 2 |  | 2 | 1 | 1.3 | N/A | 1.2 | 25.248 | 8 | 6.6 | N/A
D-DT-5207 | NECRT Support | 1 |  | 1.8 | 0.9 | 0.9 |  | 1.62 | 8.72 | 4
|  | area for new found. = |  | 54.51
| Transformer plinth |  |  | floor Area m2
D-EC-xxxx-9 | Bund wall floor | 1 |  | 34.6 | N/A | 3.46 | N/A | N/A | N/A | N/A | N/A | N/A
D-EC-1678-2 | Auxiliary transformer | 0 |  | 0 | 0 | 0 | N/A | 0 | N/A | N/A | 0 | N/A
D-EC-1678-2 | Mechanism box | 0 |  | 0 | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A
| bund wall | 34 | length in m | 15.3 | 6.885 | 3.825 | [6 empty] | 1360
|  | 0.4 | Height in m
| drainage 75mm dia pipe | 15 | length in m |  | 0.5
Yard work
KB 1157 | Bullnose edging- 1m outer fence | 195 |  |  | 7.3125 | 2.925 | 4875 | N/A | N/A | N/A | N/A | N/A
KB 1002 | cable trench curbing | 0 | 1 |  | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A
KB 1020 | Figure 8 (rollover)-road curb | 79 |  |  | 3.95 | 1.975 | 8690 | N/A | N/A | N/A | N/A | N/A
| Cable trench covers 740x300mm | 0 | 0 | N/A | N/A | N/A | N/A
| Cable corner covers 740x740mm | 0 | 0
| Main earthing | 0 |  |  | 0 | N/A | N/A | N/A | N/A | N/A | N/A
Stoning
| 9mm Road stone | 3.1 |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| 19mm yard stone | 200 |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Diamond mesh | 0 |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Barb wire | 0 |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Total qauntity | 0 |  |  | 21.236 | 15.195 | 13565 | 3.36 | 42.648 | 16 | 6.6 | 0

## Decommisioning (hidden)
Dgn no. | Description | Qauntity: compl conc. Remov. | Qauntity: below gnd | Backfill m3 | complete conc. rem m3 | exc. comp. conc. rem m3 | Concrete 100mm below gnd m3 | exc. Conc. below gnd m3 | hd bolts to be cut off | Total concrete removal
Tescor 7713/6 | 66kV Isolator foundation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tescor 7713/6 | 66kV bkr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tescor 7713/6 | 66kV Trfr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0
Tescor 7713/6 | 66kV Neutral CT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tescor 7713/6 | SA base | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Small equipment supp. (tyalara) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| foundations Tyalara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV breaker base Tyalara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.54/494 rev. 5 | 6,6-11-22kV Isolator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Smithfield VT foundation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Smithfield trfr foundation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0
0.54/4276 rev. 0 | 22kV GEC CB (dog box) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.54/308 | Medium equipment supp. foundation | 0 | 4 | 0.324 | 0 | 0 | 2.754 | 0.324 | 16 | 2.754
Cable trench |  | 0 | N/A | 0 | 0 |  | N/A |  | N/A | 0
Diamond mesh |  | 0 | N/A | N/A | N/A |  | N/A |  | N/A | N/A
Barb wire |  | 0 | N/A | N/A | N/A |  | N/A |  | N/A | N/A
Totals |  |  |  | 0.324 | 0 |  | 2.754 |  | 16 | 2.754