## BOQ
Bill of Quantities: Provision of Maintenance and Repairs to ELIDZ Pump stations
Item | Description | Unit | Qty | Supply Rate | Amount
SECTION A1 : ANNUAL CHARGES
A1.1 | Annual Preliminaries
A1.1.1 | Provision of surety | Year | 1
A1.1.2 | Provision of insurances | Year | 1
A1.1.3 | Staff protective personal equipment | Year | 1
A1.1.4 | Staff induction | Year | 1
A1.1.5 | Initial OHS compliance | Year | 1
A1.1.6 | Initial CEMP compliance | Year | 1
A1.1.7 | Provision of Electronic Maintenance Manual | Year | 1
A1.1.8 | Provision of Updated drawings in AutoCAD format | Year | 1
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION A2 : MONTHLY CHARGES
A2.1 | Monthly Preliminaries
A2.1.1 | Provide permanent on-site staff during normal working hours to undertake various maintenance and plant operation tasks as directed or required, including: 1 x Senior Technician (Mechanical) 1 x Senior Technician (Electrical) 1 x Health & Safety Officer 6 x Semi-skilled Labourers | Months | 12
A2.1.2 | Provide for all other contractual obligations, preliminaries, overheads, administrative requirements, supervision, compliance costs, and incidental items not specifically detailed above but necessary for the complete execution of the works in accordance with the contract. | Months | 12
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION B1 : ROUTINE MAINTENANCE AT SEWER PUMPSTATION
B1 | Routine Maintenance (Inclusive of All Labour, Equipment, Transport and Related Costs)
B1.1 | Carry out a complete monthly inspection of all Z1A Indoor Waste Water Pump Station assets, including mechanical, electrical, control, and associated auxiliary equipment, and submit a detailed condition report highlighting asset status, defects identified, maintenance requirements, risks, and recommended corrective actions. | No. | 12
B1.2 | Maintain and support all Sewer Pump Station equipment and associated components, including 2 × Gorman Rupp T6 pumps, 2 × 37 kW motors, 4 × non-return valves, 2 × isolation valves, suction and delivery pipework, 2 × vacuum gauges, 2 × pressure gauges, protection systems, support brackets, covers, and name plates, with application of Tectyl Marine Grade corrosion retardant, greasing, and lubricating included. | No. | 12
B1.3 | Maintain and support the Huber Rotamat R02/1000/3 Screen including electrical control panel, water supply lines, spray jets, bearings, differential level controls, and all associated fittings, inclusive of inspection, cleaning, adjustment, lubrication, fault finding, testing, and minor maintenance works required to ensure efficient and reliable operation. | No. | 12
B1.4 | Maintain and support the Main electrical distribution control panel for the plant Sewer PumpStation, including display indications, filtered ventilation, 1 × Siemens G120 variable speed drive & 1 x LS variable speed drive, protection equipment, single-line diagrams, terminal connections, and general cleaning. | No. | 12
B1.5 | Maintain, support, and calibrate Endress+Hauser Magflo, level, and differential instrumentation, including display modules, float levels, pressure transducers, and control outputs, with verification of I/O measurements required for Citect SCADA recordings and control. | No. | 12
B1.6 | Maintain, support, and calibrate the Endress+Hauser CE4 measuring station, including electronics, water sampler, analysis and protection instrumentation, pump, water supply, control outputs, and verification of I/O measurements required for Citect SCADA recordings and control. | No. | 12
B1.7 | Maintain and support the domestic electrical installation, including internal and external lighting, ventilation supplies, socket outlets, motor supplies, screen supply, and CE4 measuring station supply. | No. | 12
B1.8 | Service of 37kW Siemens Motor | No. | 2
B1.9 | Cleaning of inlet channels and wet well sump | No. | 12
SECTION B2 : ROUTINE MAINTENANCE AT MARICULTURE & SALT WATER PUMPSTATION
B2,1 | Conduct a complete monthly inspection and submit a condition report of all mariculture sea water pump station assets, including the reservoir site, detailing reconciliation of water delivery and consumption data. | No. | 12
B2,2 | Maintain and support 2 × ABS BE 425–2048 pump sets, 2 × 1LG4317–4AA60–2K20 + D60 200 kW Siemens motors (Size 315 L Therm CL 155 (F) IE1), 2 × Flygt BS 2720.390MT (241) submersible pumps, 1 × additional submersible pump, 4 × non-return valves, 19 × isolation gate valves, 2 × Bermad valves, air valves, all pipework inside the pump station, all M&E gauges, fall protection, stairways, landings, support brackets, covers, and name plates, including application of corrosion retardant, greasing, and lubricating. | No. | 12
B2,3 | Maintain and support 2 × Hydrotech drumfilters, including electrical control panels, water supply lines, jets, bearings,Grundfos vertical pumps, filter panels, and controls. | No. | 12
B2,4 | Maintain, support, and calibrate all control instrumentation at the reservoir site, including display modules, float/ultrasonic levels, pressure transducers, control outputs, and verification of I/O measurements required for Citect SCADA recordings and monitoring. | No. | 12
B2,5 | Maintain, support, and calibrate all control instrumentation at the sea water pump station, including display modules, float/ultrasonic levels, pressure transducers, control outputs, and verification of I/O measurements required for Citect SCADA recordings and monitoring. | No. | 12
B2,6 | Provide quarterly and annual certification for 2 × motorized winches and their associated chains. | No. | 2
B2,7 | Maintain and support 2 × motorized winches, including control wiring, lifting hooks, gantry, and track. | No. | 12
B2,8 | Clear and remove silt build-up around sea inlet cages in the gulley (approx. 2 m³) twice a year, remove cages, place temporary screens, clean cages, remove any debris in the inlet pipework, and re-install cages in their original position | No. | 1
B2,9 | Divers to clean and inspect quaterly | No. | 8
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION C1 : WASTE WATER PUMPSTATION
C1 | Replacement Parts - (Cost of supply, delivery and Installation)
C1.1 | LS variable speed drive H100 | Qty | 1
C1.2 | 150DN Inlet Non Return Valve | Qty | 1
C1.3 | 150DN Exit Non Return Valve | Qty | 1
C1.4 | 250DN Isolation Valve | Qty | 1
C1.5 | V Belt | Qty | 4
C1.6 | Gorman Rupp T6 Pump Air valves | Qty | 2
C1.7 | Endress+Hauser RSG35 Paperless Data Recorder. - 8 Universal Inputs, 24V - Maths Application Package. | No | 1
C1.8 | Endress+Hauser FMU90 Ultrasonic Level Transmitter. - Dual Sensor Input, 4 - 20 mA + 6 Relay - Complete with 2x FDU91 Sensor (Inlet screen differential) 1.00 48,950.00 48,950.00 4 Endress+Hauser PMP11 Pressure | No | 1
C1.9 | Endress+Hauser PMP11 Pressure Transmitter. - 0 to 16 Bar, M12 Plug - Thread G 1/2 316L Flush Mount | No | 1
C1.10 | 0 - 600 kPa Pressure Gauge with Stainless Steel Internals and 1/4" BSP Process Connection. (Outlet Pressure & Delivery Pressure) | No | 2
C1.11 | 100 - 0 kPa Vacuum Pressure Gauge with Stainless Steel Internals and 1/4" BSP Process Connection.B71 | No | 2
C1.12 | Rewiring of the Control Panel | Sum | 1
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION D1 : SALT WATER PUMPSTATION
D1 | Replacement Parts - (Cost of supply, delivery and Installation)
D1.1 | S7-1500 PLC to replace old S7-300 PLC, IM module for integration of exisiting IO to new S7-1500 and KTP1200 HMI to bring everything into current TIA platform | Sum | 1
D1.2 | Installation and re-programming of new PLC in TIA portal, onsite commissioning of PLC & rewiring of necessary compnents in panel | Sum | 1
D1.3 | 350DN NRV | Qty | 1
D1.4 | 350DN Gate valves | Qty | 2
D1.5 | 350DN Bermad valve | Qty | 2
D1.6 | Sub pump floor standing (7.5kW) | Qty | 1
D1.7 | 350DN Non return valves (800mm Long) | Qty | 2
D1.8 | Dry well pumps (5.5kW) | Qty | 2
D1.9 | Vacuum Gauge | Qty | 2
D1.10 | Pressure Gauge | Qty | 2
D1.11 | Wet well sub pump (5.5kW) | Qty | 1
D1.12 | 350DN Sea isolating valve | Qty | 2
D1.13 | Endress+Hauser Promag W10 DN300 Magflow. - 24 vDc, 4 - 20 mA + Pulse - Remote Display 25m cable - PN16 Stainless Steel Flange, Alloy C22 Electrodes - IP68 Factory Potted, corrosion protection sensor (Pump 1 & 2) | No | 2
D1.14 | Endress+Hauser FMU90 Ultrasonic Level Transmitter. - Single Sensor Input, 4 - 20 mA + 1 Relay - Complete with 1x FDU91 Sensor (Water Level ion Wet Well) | No | 1
D1.15 | Endress+Hauser Ultrasonic CUS71D Sludge/Sand Level Sensor complete with CM442 Multi Parameter Liquid Analyzer Transmitter. - 220Vac, 4 - 20 mA Output | No | 1
D1.16 | Endress+Hauser PTC31B Pressure Switch. - 0 to 10 bar, PNP + 4 - 20 mA Output - Thread G1/2 316L (Pump Line 1 & 2, Delivery Line 1 & 2) | No | 4
D1.17 | 0 - 600 kPa Pressure Gauge with Stainless Steel Internals and 1/4" BSP Process Connection with Chemi-seal. (Pump 1 & 2) | No | 2
D1.18 | Wet well sub pump (5.5kW) | No | 1
D1.19 | Dry well pumps (5.5kW) | No | 1
D1.20 | Endress+Hauser Promag W400 Ultrasonic Clamp-on Flow Meter. - 100...240 Vac / 240 vDc, 4 - 20 mA + Pulse - 15m cable, remote housing - Installation set included | No | 2
D1.21 | Knife gate valve Orings seals | No | 40
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total
Item | Description | Unit | Qty | Supply & Install Rate | Amount
SECTION E1 : PROVISIONAL SUMS
E1.1 | Call out (inclusive of all labour, equipment, transport and related costs)
E1.1.1 | Emergency response (Immediate) | hr | 300
E1.1.2 | Urgent response (24 hours) | hr | 300
E1.1.3 | Routine response (extra over during normal working hours) | hr | 300
E1.2 | Labour additional to scheduled works
E1.2.1 | Mechanical Technician/ Electrical Technician | hr | 480
E1.2.2 | Semi Skilled Labour | hr | 480
E1.2.3 | Labour | hr | 480
E1.3 | Travelling additional to scheduled works
E1.2.1 | LDV | hr | 50
E1.2.2 | Truck - 8 Ton | hr | 20
E1.2.3 | Hydraulic Platform | hr | 5
E1.2.4 | Crane truck | hr | 5
E1.2.5 | Compressor | hr | 5
E1.2.6 | Whacker Rammer Compactor | hr | 5
E1.4 | Provisional Allowance for replacement equipment
E1.4.1 | Contingency allowance for non-schedule Work | Sum | 1 | 20000 | 20000
E1.4.2 | Profit and Attendance | %
TOTAL FOR SCHEDULE CARRIED FORWARD TO SUMMARY |  |  |  | Sub Total
SUMMARY
SECTION A1 : ANNUAL CHARGES
SECTION A2 : MONTHLY CHARGES
SECTION B1 : ROUTINE CHARGES
SECTION C1 : WASTEWATER PUMPSTATION
SECTION D1 : SALT WATER PUMPSTATION
SECTION E1 : PROVISIONAL SUMS
|  | Escal (%) | Sub-total ( R) | Escal (R)
Nett Tender Sum for Year 1
| Nett Tender Sum for Year 2 (A1+A2+B1+E1) Escalated | %
Sub-total
Add VAT @ 15%
Gross Tender Sum carried to Form of Offer

## Assets
Item | Description | Unit | Qty | Supply & Install Rate
SECTION F1 : GENERAL MAINTENANCE
F1 | General maintenance (inclusive of 24 hour response with ELIDZ control and security office)
| SECTION F: WASTE WATER PUMPSTATION | Qty | 1
|  | Qty | 1
F1.1 | G6 PIONEER ROTATING set | Qty | 1
F1.2 | GR T6 Seals Pump - No. 1 | Qty | 1
F1.3 | New Booster pumps S/steel | Qty | 1
F1.5 | Mains Supply indication | Qty | 1
F1.6 | FDU 80 instrument | Qty | 1
F1.7 | FDU 80 display | Qty | 1
F1.8 | Magflo meter | Qty | 1
F1.9 | Paperless recorder | Qty | 1
F1.10 | 24 Volt power supply | Qty | 1
F1.11 | 24 Volt relays | Qty | 1
F1.12 | 1 Phase 200A Isolator + interlock | Qty | 1
F1.13 | 1 Phase 100 A MCB | Qty | 1
F1.14 | 1 Phase 80 A MCB | Qty | 1
F1.15 | 1 Phase 10 A MCB | Qty | 1
F1.16 | 1 Phase 10 A MCB | Qty | 1
F1.17 | 1 Phase Surge Protection | Qty | 1
F1.18 | 1 Phase ELU 50 A | Qty | 1
F1.19 | Single Phase ELU 60 A | Qty | 1
F1.20 | Single Phase 10 A MCB | Qty | 1
F1.21 | Single Phase 20 A MCB | Qty | 1
F1.22 | Single Phase 10 A MCB | Qty | 1
F1.23 | 60 A Welding Outlet | Qty | 1
F1.24 | 16 A Single Switched Socket Outlet | Qty | 1
F1.25 | 16 A Double Switched Socket Outlet | Qty | 1
F1.26 | Type A - Nordland / JB258 / C21 / ECG / Warm Start / SS clips | Qty | 1
F1.27 | 58 Watt Fluorescent Lamp 1.5m | Qty | 1
F1.28 | Air Release valve ?? | Qty | 1
F1.29 | Pump piping for 2nd PIONEER sets | Qty | 1
F1.30 | Genset service VOLVO( Needs to be set on Auto mode. It does not kick in when power is off). | Qty | 1
F1.31 | Repair of steel piping suction and delivery | Qty | 1
F1.32 | Pipe Supporting Steel Stands | Qty | 1
F1.33 | New Panel main MCC | Qty | 1
F1.34 | New Sump for holding WWTW complete with valves and valve chamber | Qty | 1
F1.35 | LS variable speed drive H100 | Qty | 1
G1 | General maintenance (inclusive of 24 hour response with ELIDZ control and security office) | Qty | 1
|  | Qty | 1
| SECTION G1: SEA WATER PUMP STATION | Qty | 1
|  | Qty | 1
G.1.1 | Emergency sand pumps in main chamber | Qty | 1
G.1.2 | Hoist service | Qty | 1
G.1.3 | Inlet Pipe line - 316 s/steel duplex | Qty | 1
G.1.4 | Vacuum Gauge | Qty | 1
G.1.5 | Pressure Gauge | Qty | 1
G.1.6 | Isolating valve ULTRA | Qty | 1
G.1.7 | ABC Pump new | Qty | 1
G.1.8 | Siemens Motor new | Qty | 1
G.1.9 | Motor and Pump coupling new | Qty | 1
G.1.10 | Gate valves | Qty | 1
G.1.11 | Bermad valve | Qty | 1
G.1.12 | Sub pump floor standing 1.5KW | Qty | 1
G.1.13 | Booster pump 0.75kw | Qty | 1
G.1.14 | Dry well pumps 5.5kw | Qty | 1
G.1.15 | DN350 Isolating valve ULTRA | Qty | 1
G.1.16 | Emergency sub pump in the incoming chaimber | Qty | 1
G.1.17 | Hoist service | Qty | 1
G.1.18 | Air Release valve | Qty | 1
G.1.19 | Inlet Pipe line - TO BE PRICED AS NEEDED 316 s/steel duplex | Qty | 1
G.1.20 | Vacuum Gauge | Qty | 1
G.1.21 | Pressure Gauge | Qty | 1
G.1.22 | Wet well sub pump 5.5kw | Qty | 1
G.1.23 | Genset service VOLVO | Qty | 1
G.1.24 | ABC pump service | Qty | 1
G.1.25 | Siemens Motor service | Qty | 1
G.1.26 | Lights inside building | Qty | 1
G.1.27 | Lights outside building day and night switches | Qty | 1
G.1.28 | Air valves top | Qty | 1
G.1.29 | Flow meters | Qty | 1
G.1.30 | Pressure gages pumps | Qty | 1
G.1.31 | Piping to and from gages | Qty | 1
G.1.32 | Sea intake valve service | Qty | 1
G.1.33 | Sea isolating valve service | Qty | 1
G.1.34 | Sea intake valve new | Qty | 1
G.1.35 | Sea isolating valve new | Qty | 1
G.1.36 | PVC piping / plumbing repairs / new | Qty | 1
G.1.37 | PVC valves new | Qty | 1
G.1.38 | SUB pump suction hoses NEW - Dry well pump | Qty | 1
G.1.39 | SUB pump suction hoses NEW - Wet well pump | Qty | 1
G.1.40 | Sea intake sump, to clean and assess (1 week) | Qty | 1
G.1.41 | Main SIEMENS PLC to communicate with all in auto | Qty | 1
All repairs under General maintenance will be catered for under Provisional sums with quotations based on their submitted prices